City of Tekoa
Wastewater Treatment Plant Facility Plan

Engineering Report

July 2025

30393.041.01

Prepared for:
The City of Tekoa

Prepared by:
Century West Engineering
11707 E Montgomery Drive

Spokane Valley, WA 99206

City of Tekoa
Wastewater Treatment Plant Facility Plan

Engineering Report
30393.041.01

| Prepared for: The City of Tekoa Prepared by: Century West Engineering 11707 E Montgomery Drive Spokane Valley, WA 99206 |  |
| --- | --- |

Table of Contents

1	INTRODUCTION	19

1.1	Regulatory Requirements	19

1.2	Agency Information	22

1.3	Issues and Objectives	22

2	DISCHARGE STANDARDS	24

2.1	Existing Permit	24

2.2	Limits	24

2.3	Compliance History	25

2.4	Watershed Considerations	27

2.4.1	Hangman Creek Watershed Study	27

2.4.2	Tekoa Receiving Water Study	Error! Bookmark not defined.

3	BACKGROUND INFORMATION	32

3.1	Environmental	32

3.1.1	Floodplains	Error! Bookmark not defined.

3.1.2	Wetlands	32

3.1.3	Shoreline	36

3.1.4	Endangered Species/Habitat	38

3.1.5	National Wild and Scenic Rivers Act	39

3.2	Community Considerations	Error! Bookmark not defined.

3.2.1	Community Health	Error! Bookmark not defined.

3.2.2	Archeological and Historical	40

3.3	Land Use and Zoning	40

3.4	Urban Growth Areas and Future Development Trends	42

3.5	Tekoa Area Geography and Landscape	43

3.6	Tekoa Water System Description	43

3.6.1	Water Sources	43

3.1.1	Water Storage	44

3.6.2	Distribution System	44

3.6.3	3.6.1 Water Sources	44

3.7	Population Growth and Projections	45

3.7.1	Population Data Sources	45

3.7.2	Demographic and Housing Analysis (2014-2024)	45

3.7.3	Comparison of Demographic and Housing Trends: Whitman County Vs. Tekoa	48

3.7.4	Comparison of Demographic and Housing Trends: Spokane County Vs. Tekoa	51

3.8	Population Projection Methodology	54

3.8.1	Data Sources	54

3.8.2	Method 1: WAOFM’s growth projection	54

3.8.3	Method 2: Decennial Census Data	55

3.8.4	Method 3: Intercensal Data	56

3.8.5	Method 4: Spokane County Population Trends	57

3.8.6	Methods 5 & 6: Housing Unit – Based Projection	58

3.9	Summary and Conclusion	61

3.10	Conclusion	Error! Bookmark not defined.

4	PRESENT WASTEWATER CONDITIONS	62

4.1 Waste Loading	63

4.2  Wastewater Sources	64

4.3 Infiltration and Inflow Assessment	64

4.1	Load and Flow Variations	64

4.1.1	Seasonal	64

4.1.2	Diurnal	64

5	Existing and Projected Wastewater Characteristics	65

5.1	Introduction	65

5.2	Wastewater Flow Characteristic Terms	65

5.3	Wastewater Flow Summary	1

5.3.1	ERU Calculations	2

5.3.2	Wastewater ERU	2

5.4	Inflow and Infiltration Analysis	2

5.4.1	Estimating Average Base Sanitary Flow (BSF)	2

5.4.2	Peak Hour Flow	3

5.4.3	Minimum Flow	5

5.4.4	Dry Weather Flow	5

5.4.5	Wet Weather Flow	8

6	Alternatives Analysis	11

6.1	Land-Based Disposal Methods	11

6.1.1	No-Action Alternative	11

Appendices

- Tekoa NPDES Permit (WA0023141)

- Flow Calculations

- Population Projection Calculations

- Flood Plain Map

- Priority Habitat and Species (PHS) Report

- US Fish and Wildlife Service (USFWS) Species List

- Wetlands Map

- USDA Soil Report

- County Parcel Maps

Abbreviations & Acronyms

CAO: 		Critical Areas Ordinance

ECY: 		Washington State Department of Ecology

DOH: 		Washington State Department of Health

LOSS: 		Large On-Site Sewage System

MDF: 		Maximum Daily Flow

PHF: 		Peak Hourly Flow

PVC: 		Polyvinyl Chloride

SEPA: 		State Environmental Policy Act

TDH: 		Total Dynamic Head

WAC: 		Washington Administrative Code

WSDOT: 	Washington State Department of Transportation

I. Regulatory Requirements for FACILITY PLAN/Engineering Reports

This Wastewater Treatment Plant Facility Plan (Facility Plan) has been prepared for the City of Tekoa, Washington, in accordance with the provisions of Washington Administrative Code (WAC) Chapter 173-240, "Submission of Plans and Reports for Construction of Wastewater Facilities." The WAC requirements for an engineering report (as detailed in WAC 173-240-060) are listed in the table below, cross-referenced to their location within this document. Technical guidance was also drawn from the Washington State Department of Ecology's (Ecology) "Criteria for Sewage Works Design" (Orange Book).

| Text from WAC 173-240-060 | Inclusion Check | Confirmation / Location |
| --- | --- | --- |
| 060(1) Planning Requirements |  |  |
| The engineering report for a domestic wastewater facility shall include each appropriate (as determined by Ecology) item required in WAC 173-240-050 for general sewer plans unless an up-to-date general sewer plan is on file with Ecology. Normally, an engineering report is not required for sewer line extensions or pump stations. See WAC 173-240-020(13) and 173-240-030(5). The facility plan described in 40 CFR 35 is an “engineering report." | The report complies with an up-to-date general sewer plan (WAC 173-240-050) approved by and on file with Ecology, OR the report includes required portions of WAC 173-240-050 as determined through consultation with Ecology if an adequate plan is not on file. | No |
|  | General sewer plan adequately addresses the current conditions and service area. (If applicable and plan is on file) | Yes |
| 060(2) Sufficiently Complete |  |  |
| The engineering report shall be sufficiently complete so that plans and specifications can be developed from it without substantial changes. | The report contains sufficient design information to allow an engineer not involved in writing the report to produce construction drawings for the facility without reevaluation of the selected unit processes or more than minor unit sizing modifications. | Yes |
| 060(3) Minimum Information Required |  |  |
| (a) The name, address, and telephone number of the owner of the proposed facilities, and their authorized representative. | The report includes the name, address, and telephone number of the owner and the owner's authorized representative. | Section 1.2 |
|  | The named authorized representative or position has the authority to sign contracts relating to this project. | Section 1.2 |
|  | A specific project contact person other than the legal representative is identified. | Section 1.2 |
| (b) A project description including a location map and a map of the present and proposed service area. | The project description includes the “where, what, and why” of the report and documents the need for the proposed project. |  |
|  | Planning information established in the approved general sewer plan is referenced, and supplemented or updated as necessary to support the project-specific decisions. |  |
|  | A location map of the project area is included. |  |
|  | A map showing the current and proposed sewer service areas is included. |  |
|  | At least one map is scaled to show the complete, current, and proposed service areas along with the relationship of this service area to adjacent service areas. |  |
|  | A map showing the existing collection system changes and proposed locations of land applications of wastewater is included. (If applicable) |  |
|  | Office of Financial Management (OFM) or other population data for the service area for at least the last two decades is provided (if available). |  |
|  | Population projections for the project planning area and concentrated growth areas for the project design period are included. |  |
|  | Population projections are based on historical records cited in the approved general sewer plan and are consistent with data from appropriate local land use planning agencies. |  |
| (c) A statement of the present and expected future quantity and quality of wastewater, including any industrial wastes which may be present or expected in the sewer system. | The analysis of current conditions includes characterization of waste loading. |  |
|  | Any constituents that may have a detrimental impact on proposed unit processes are identified and discussed. |  |
|  | The distribution of wastewater sources (domestic, commercial, industrial) is included, ideally expressed as percentages. |  |
|  | Characteristics of industrial discharges and any pretreatment requirements are discussed. (If applicable) |  |
|  | Current I/I flows are included. |  |
|  | Flows received from combined sewers are included and assessed. (If applicable) |  |
|  | An assessment of diurnal flow and loading variations is included. |  |
|  | An assessment of seasonal load and flow variations is included. |  |
|  | The analysis includes at least one full year of current wastewater flow and loading data to justify appropriate design parameters. |  |
|  | The analyzed data includes sufficient detail to demonstrate the degree of flow and loading variability experienced. |  |
|  | The location of influent and effluent sampling and the type of samples taken are identified. |  |
|  | The locations of treatment process return streams are identified. |  |
|  | The report relies on credible and accurate data using laboratory data from an Ecology-accredited laboratory and flow data from meters with a documented history of proper calibration. |  |
|  | Future (normally 20 years) waste load and sources of wastewater are estimated. |  |
|  | Future estimates are based on present conditions and expected future conditions accounting for zoning patterns, council of government’s population forecasts, historical population trends, existing industrial users, and anticipated future sources. |  |
|  | Future estimates account for the anticipated impacts of existing or planned water conservation measures on future sewer service, considering potential increased waste load concentrations and per capita flow. |  |
|  | Future estimates account for the impact climate change may have on unmitigated I/I flows. |  |
|  | For facilities receiving flows from combined sewers, the assessment includes how efforts to control CSOs impact anticipated future flows. (If applicable) |  |
| (d) The degree of treatment required based upon applicable permits and regulations, the receiving water, the amount and strength of wastewater to be treated, and other influencing factors. | A copy of the current discharge permit and any compliance orders are included. (If applicable) |  |
|  | For new discharges, requirements reasonably anticipated in a draft permit are included. (If applicable) |  |
|  | The evaluation results of Sections 3(e), (h), and (I) are used to estimate the degree of treatment needed to meet conditions of a current or anticipated future permit. |  |
|  | The evaluation considers the potential for regulatory changes that could require more stringent treatment requirements during the operating life of the facility. |  |
|  | The evaluation confirms whether the level of treatment produces a discharge that complies with applicable water quality criteria in Chapter 173-201A WAC. |  |
|  | For municipal WWTPs, an analysis of conventional pollutants (BOD5, TSS, pH, dissolved oxygen, temperature) is included. |  |
|  | For municipal WWTPs, an analysis of pathogens (Enterococci, E. Coli, or Fecal Coliform bacteria) is included. |  |
|  | For municipal WWTPs, an analysis of toxic pollutants commonly present (ammonia, chlorine) is included. |  |
|  | An evaluation of the effects of industrial discharges on final effluent quality and potential for toxic materials to pass through is included. (If applicable) |  |
|  | If the receiving water is on the 303(d) list as impaired, the analysis includes the parameters identified in the impairment listing. |  |
|  | Design values align with waste load allocations established in an approved TMDL. (If applicable) |  |
|  | When Ecology has not established a waste load allocation for an impaired parameter, the analysis demonstrates no reasonable potential to cause or contribute to a water quality standard violation. |  |
|  | The report demonstrates whether the discharge will cause a measurable change in existing water quality at the boundary of any authorized chronic mixing zone (as defined by Ecology's measurable change criteria). |  |
|  | Consultation with regional Ecology staff to determine the level of analysis needed to comply with Antidegradation provisions (WAC 173-201A-300 to 330) has occurred and the analysis is included. |  |
| (e) A description of the receiving water, applicable water quality standards, and how water quality standards will be met at the boundary of any applicable dilution zone. (173-201A-10Q WAC) | The name, location (river mile, latitude/longitude, waterway segment number, township/range, etc.), and water quality classification of the proposed receiving water are provided. |  |
|  | Any existing receiving water data available from long term monitoring stations or site-specific monitoring collected for this report is summarized. |  |
|  | If site-specific monitoring data was collected for this report, it is included in an appendix. |  |
|  | For freshwater streams and rivers, the 7Q10 flow is determined and provided. (If applicable) |  |
|  | For freshwater streams and rivers, the physical characteristics of the river or stream at the 7Q10 flow and any features impacting flow near the outfall are described. (If applicable) |  |
|  | For saltwater and estuaries, the depth of the outfall at mean lower low water (MLLW), current direction and velocity profiles, and profiles for salinity, density, and temperature are determined and provided. (If applicable) |  |
|  | The potential impacts on designated uses of the receiving water from conventional and toxic pollutants reasonably expected in the effluent are evaluated. |  |
|  | The applicable numerical and narrative Water Quality Criteria found in chapter 173-201A WAC are evaluated, and the criteria that are limiting for this discharge are determined. |  |
|  | A discussion of the receiving water identifies the various chemicals that may be present and the aquatic species present to assess the need or frequency of biomonitoring WET testing. (If applicable) |  |
|  | For saltwater, the impacts of microbial (bacteria & virus) discharges on shellfish beds are evaluated. (If applicable) |  |
|  | For groundwater discharges, the minimum requirements of the hydrogeologic study are addressed (listed in E3-4 and described in the Implementation Guidance). (If applicable) |  |
| (f) The type of treatment process proposed, based upon the character of the wastewater to be handled, the method of disposal, the degree of treatment required, and a discussion of the alternatives evaluated and the reasons they are unacceptable. | A reasonable number of feasible alternatives for achieving the project goals are identified and evaluated. |  |
|  | A preferred alternative is selected, and preliminary engineering details for it are developed. |  |
|  | The alternatives evaluation considers conventional treatment technologies, advanced treatment systems, land treatment systems/lagoons (where appropriate), and treatment at regional facilities. |  |
|  | The alternatives evaluation considers alternate facility siting, no discharge alternatives, options for reclaimed water production, and nonstructural alternatives. (If applicable) |  |
|  | A no action alternative is included, and the consequences of taking no action are discussed. |  |
|  | Any water, energy, and/or waste conservation measures considered in the proposed alternatives are discussed. (If appropriate) |  |
|  | The alternatives analysis evaluates feasibility based on environmental impact, present worth cost effectiveness, technical complexity, availability of certified operators, project risk, legal and regulatory barriers, and other criteria deemed important to the community. |  |
|  | Efforts made to engage with the community on the development and evaluation of alternatives are described. |  |
|  | Community engagement efforts included discussions of the project need, feasible technologies, environmental impacts, community impacts, environmental justice, rate impacts, and other topics identified as important. |  |
|  | Reasons for rejecting alternatives from consideration are discussed. |  |
|  | If the alternative with the lowest estimated life cycle cost is not selected, the rationale for the decision is discussed, including community support for the selected alternative. (If applicable) |  |
| (g) The basic design data and sizing calculations of each unit of the treatment works. Expected efficiencies of each unit, the entire plant, and character of effluent anticipated. | Preliminary design data and sizing calculations are provided for all final alternates considered as part of the ranking process. |  |
|  | This data is used to estimate construction costs and operation and maintenance costs for life cycle cost comparisons and the alternatives analysis. |  |
|  | Detailed sizing calculations and design criteria used for sizing the selected alternative treatment systems agree with the appropriate chapters of this manual or other authoritative references. |  |
|  | Expected efficiencies of each unit of the treatment works, the entire plant, and anticipated effluent character are provided. |  |
| (h) Discussion of the various sites available and the advantages and disadvantages of the site(s) recommended. The proximity of residences or developed areas to any treatment works. The relationship of a 25-yearand 100-year flood to the treatment plant site and the various plant units. | The suitability of potential facility locations is evaluated as part of the alternatives evaluation process, assessing topography, flood potential, wetland impacts, soils suitability, zoning, environmental justice, historical/archeological impacts, community impacts, and proximity to residential areas. |  |
|  | Flood analysis goes beyond just referencing FEMA FIRM maps and includes evaluation of flooding potential from any nearby drainage way. |  |
|  | The existence and extent of wetlands on a proposed site are shown on the site map. (If applicable, may require a wetlands specialist). |  |
|  | Wall and floor elevations are compared to potential 100-year flood elevations to ensure basins are not over-topped or buildings flooded. |  |
|  | Consideration is given to using a continuous hydrologic and hydraulic model for evaluating hydraulic capacity and flooding potential. (If appropriate) |  |
|  | For coastal sites, future flooding risks associated with projected sea level rise and inundation risk due to tsunamis are considered, citing studies and discussing uncertainties. (If applicable) |  |
|  | Site assessments consider the potential impacts to historic properties or the risks of impacting archeological and culturally sensitive sites, including consultation with relevant agencies. |  |
|  | Adequate soils analyses are conducted at the final alternate sites during the site assessment stage to understand soil ability to support structures or provide treatment, including enough analysis to limit potential for changed site conditions. |  |
| (i) A flow diagram showing general layout of the various units, the location of the effluent discharge, and a hydraulic profile of the system that is the subject of the engineering report and any hydraulically related portions. | Flow diagrams showing general layout are developed for each of the final alternates considered. |  |
|  | A schematic flow diagram showing all wastewater liquid and solids flow paths, including return or recycle flows, is included. |  |
|  | Proposed compliance sampling and flow monitoring locations are included, and it is demonstrated that they will provide representative data not influenced by return/recycle flows and without unmonitored flows. |  |
|  | A scaled site layout is included that includes site topography and shows how proposed treatment units fit on the land available. |  |
|  | A detailed hydraulic profile for the selected alternate is developed. |  |
|  | The hydraulic profile includes the high plant flow, high receiving water flow/elevation, and low plant flow conditions. |  |
|  | Hydraulic profiles are included for other critical flow conditions if necessary to justify unique design elements or operating conditions. (If applicable) |  |
| () A discussion of infiltration and inflow problems, overflows and bypasses, and proposed corrections and controls. | The existing treatment plant flows are evaluated to show the degree of I/I in the collection system, including a review of system age/characteristics, flow monitoring, and location of high I/I lines. |  |
|  | The evaluation includes at least one year of testing to establish baseline flows and conditions if needed per C1-7 guidance. (If applicable) |  |
|  | How I/I impacts the overall facility design and performance is described. |  |
|  | Alternatives for minimizing or mitigating existing and anticipated future I/I are described and evaluated, including collection system rehabilitation, equalization basins, or accounting for variability in design. |  |
|  | The report demonstrates that the proponent considered the impacts of high I/I when evaluating the appropriateness of alternative treatment technologies. |  |
|  | Discharge locations for anticipated SSOs and CSOs are identified on a map, and their current frequency and impacts on receiving water are discussed. (If applicable) |  |
|  | Recommendations for eliminating SSOs are discussed. |  |
|  | How the project relates to CSOs control efforts is described. (If applicable) |  |
|  | The report does not propose plans that result in increased frequencies or impacts of SSO and/or CSO discharges. |  |
|  | The proposed project is consistent with an approved CSO control plan. (If applicable) |  |
| (k) A discussion of any special provisions for treating industrial wastes, including any pretreatment requirements for significant industrial sources. | Any required special handling by the treatment plant and proposed methods for handling industrial wastes identified in 3(c) are discussed. (If applicable) |  |
|  | Appropriate treatability studies are referenced for existing industrial wastewaters to identify the potential to interfere with proposed unit processes. (If applicable) |  |
|  | The extent of industrial pretreatment needed to ensure stable plant operation, suitability of biosolids for beneficial use, and water quality protection is identified. |  |
|  | Pretreatment requirements for significant industrial sources are discussed. (If applicable) |  |
| (l) Detailed outfall analysis or other disposal method selected. | The location of the existing or proposed outfall and diffuser design are identified. |  |
|  | A preliminary analysis of the outfall is provided to assess impacts on the receiving water described in 3(e). |  |
|  | A sufficiently detailed outfall analysis is provided to justify that the proposed discharge will comply with water quality standards at the point of discharge or at the boundaries of acute and chronic mixing zones (if allowed). |  |
|  | The analysis is consistent with Ecology’s “Guidance for Conducting Mixing Zone Analyses” and EPA's “Technical Support Document for Water Quality-based Toxics Control”. |  |
|  | The analysis includes all critical flow and loading situations expected for the facility. |  |
|  | For discharges to rivers and river-like estuaries, the low flow represents the 7Q10 flow or other regulated low flow. (If applicable) |  |
|  | For marine discharges, the analysis uses mean lower low water elevation and seasonal conditions that result in the greatest stratification in the water column. (If applicable) |  |
|  | If the outfall construction or reconstruction project is located on state owned aquatic land, this is identified, and how the project complies with any DNR requirements and communication with DNR are described. (If applicable) |  |
|  | The outfall and diffuser are included in the basic design data for 3(g). |  |
|  | If wastewater land application is the disposal method, this is addressed referencing section 060(4). (If applicable) |  |
| (m) A discussion of the method of final sludge disposal and any alternatives considered. | A residual solids management plan is included that evaluates expected solids quantities and quality, and potential beneficial use options. |  |
|  | The management plan evaluates sludge treatment options at the plant and relates these to the biosolids use options. |  |
|  | The plan ensures compliance with applicable state and federal laws/regulations (40 CFR 503, WAC 173-308), Ecology’s Minimal Functional Standards, and local permits. |  |
|  | If disposal in a solid waste landfill is proposed, it is justified that no feasible beneficial use options exist and disposal complies with requirements of 40 CFR 258 and WAC 173-351. (If applicable) |  |
|  | A solids mass balance for the treatment plant is determined as part of the process of developing and comparing alternatives. |  |
|  | A ranking of residual solids handling alternatives is presented, identifying the preferred alternative, actions necessary for implementation, and reasons for not selecting other alternatives. |  |
| (n) Provision for future needs. | The proponent discusses the future wastewater needs of the community with an emphasis on identifying potential alternatives to accommodate future growth. |  |
|  | The discussion includes the potential to expand an existing treatment plant on a given site, constructing a new plant on an alternate site (including locations), and the ability to extend the sewerage system. |  |
|  | Population, industrial, and commercial growth expectations for the service area are identified, considering high, medium, and low growth profiles. |  |
| (o) Staffing and testing requirements for the facilities. | The comparison of alternatives discusses the potential staffing needs (levels and specialization) of each final treatment alternative. |  |
|  | Justification is provided that the plan includes a sufficient number of staff with appropriate experience to successfully operate the facility at all times. |  |
|  | The proposed facility’s classification under Chapter 173-230 WAC is identified, and it is indicated that staffing includes at least one operator matching the classification as the operator in responsible charge. |  |
|  | The number and responsibilities for individuals not considered certified operators (for instance, administrative, mechanics, technicians, electricians, lab staff not responsible for process control decisions) are discussed. |  |
| (p) An estimate of the costs and expenses of the proposed facilities and the method of assessing costs and expenses. The total amount shall include both capital costs and also operation and maintenance costs for the life of the project, and shall be presented in terms of total annual cost and present worth. | The report presents the engineer's best opinion of probable final costs, describing methods used to develop estimates and including an opinion of expected accuracy. |  |
|  | The level of accuracy falls within the Class 3 to Class 4 ranges established by AACE International (no less than -30% to at least +50%). |  |
|  | The cost estimate accounts for all anticipated costs associated with the project (construction, land acquisition, engineering, permits, soft costs). |  |
|  | Any value engineering reviews completed prior to formulating the cost estimate are discussed, including whether further review may occur during design. |  |
|  | A present worth analysis of O&M costs is included for each of the final alternates as part of the ranking process, with a rough breakdown by O&M category. |  |
|  | The required user charges are calculated to support the estimated costs of the selected alternative. |  |
|  | The estimate of user rates includes assumptions about potential grant funding, and the user rate assuming no grant funding is presented for comparison. |  |
|  | Information about current rate schedules, annual O&M cost (with energy breakout), other capital improvement programs, tabulations of users by monthly usage categories, status of existing debts, and required reserve accounts is provided. |  |
| (q) A statement regarding compliance with any applicable state or local water quality management plan or any such plan adopted pursuant to the federal Water Pollution Control Act as amended. | Any applicable state or local water quality management plan connected to the proposed project is identified, and how the project is connected to that plan is discussed. |  |
| (r) A statement regarding compliance with SEPA and NEPA, if applicable. | An environmental report identifying potential environmental impacts is included, along with a copy of the completed SEPA checklist and appropriate adopted SEPA determination. |  |
|  | The SEPA process demonstrates appropriate public participation in project decision-making, including descriptions of the approach used to engage the community on project need, service levels, funding, and environmental/societal considerations. |  |
|  | It is indicated that the local government made the final SEPA determination prior to approval of the engineering report. |  |
|  | If the project may qualify for a categorical exemption from SEPA, the report clearly describes how it aligns with the exemption allowance. (If applicable) |  |
|  | If federal funding or action by a federal agency is anticipated, the report discusses whether the project must comply with NEPA. (If applicable) |  |
| 060(4) Land Application Discharges |  |  |
| The engineering report for projects utilizing land application, including seepage lagoons, irrigation, and subsurface disposal, shall include information on the following together with appropriate parts of subsection C(3) of this table, as determined by Ecology: | The report addresses a project utilizing land application (seepage lagoons, irrigation, and/or subsurface disposal) and is not classified as a Large On-site Sewage System under WAC 246-272B/RCW 70.118B. |  |
|  | Appropriate parts of subsection 060(3) are included, as determined by Ecology. |  |
|  | The reasonability test (WAC 173-240-035 restriction on subsurface disposal) is satisfied by addressing the requirements below. (If subsurface disposal is considered) |  |
| (a) Soils and their permeability. | Information on the soils and their permeability in the land application area is included. |  |
| (b) Geohydrologic evaluation of such factors as: (i.) Depth to ground and ground water movement during different times of the year. (ii.) Water balance analysis of the proposed discharge area. (Hi.) Overall effects of the proposed facility upon the ground water in conjunction with any other land application facilities that may be present. | A geohydrologic evaluation is included addressing: depth to ground and ground water movement throughout the year, a water balance analysis of the discharge area, and overall effects on groundwater in conjunction with other facilities. |  |
|  | The ground water quality criteria are determined using Chapter E3 guidance. |  |
| (c) Availability of public sewers. | The availability of public sewers connected to a conventional treatment facility is discussed, and the selection process demonstrates consideration of long-term reliability. (If applicable) |  |
| (d) Reserve areas for additional subsurface disposal. | If subsurface disposal is selected, adequate area for 100% replacement of the drain field is demonstrated, consistent with WAC 246-272B. (If applicable) |  |

# INTRODUCTION

This Wastewater Treatment Plant Facility Plan (Facility Plan) provides a comprehensive assessment and strategic roadmap for the City of Tekoa, Washington's wastewater infrastructure over the next 20 years. It thoroughly evaluates the existing collection, treatment, and disposal systems, identifies current deficiencies and future needs, and recommends the most cost-effective and compliant path forward. The analysis includes a detailed comparison of potential improvement scenarios against a no-action alternative to guide the City's decisions on essential wastewater system investments.

In addition, this report fulfills the Washington Administrative Code (WAC) 173-240-050, which requires an up to date General Sewer Plan in order to consider changes to the existing system such as the ones proposed in this Engineering Report.

## Regulatory Requirements Summary

This Facility Plan is developed in accordance with the requirements outlined in Washington Administrative Code (WAC) Chapter 173-240, "Submission of Plans and Reports for Construction of Wastewater Facilities," particularly WAC 173-240-060 which details the required engineering report content. It also considers design standards and guidance from the Washington State Department of Ecology's (Ecology) "Criteria for Sewage Works Design" (Orange Book), relevant surface water quality standards (WAC 173-201A), groundwater quality standards (WAC 173-200), and federal secondary treatment regulations. The table presented in the preliminary section cross-references specific WAC 173-240-060 requirements to their location within this report.

## Planning Requirements

Wastewater systems in Washington State follow a comprehensive regulatory framework that spans from initial planning through operational monitoring. During the planning phase, the Department of Ecology maintains oversight authority by requiring approval of general sewer plans, engineering reports, and construction plans and specifications before any construction activities commence. The specific content requirements and sequencing for these submittals are established in WAC 173-240 and the Criteria for Sewage Works Design (Orange Book, CSWD). Environmental review under the State Environmental Policy Act (SEPA) must be completed during the planning phase prior to obtaining Ecology approvals, with additional State Environmental Review Process (SERP) or National Environmental Policy Act (NEPA) requirements applying when federal funding is involved.

## Design Requirements

Design standards for wastewater facilities must demonstrate reasonable consistency with CSWD guidelines, though Ecology recognizes alternative design references from professional organizations including the Water Environment Federation (WEF), American Society of Civil Engineers (ASCE), American Public Works Association (APWA), and Environmental Protection Agency (EPA) for design review purposes. Projects incorporating water reclamation components must additionally comply with WAC 173-219 (Purple Book) and require coordination with both Ecology and the Department of Health.

## Permitting Requirements

The permitting framework encompasses multiple regulatory programs depending on the discharge type and receiving environment. National Pollutant Discharge Elimination System (NPDES) permits are required for surface water discharges, with Ecology serving as the delegated permitting authority. State Waste Discharge (SWD) permits govern discharges to ground and certain discharges to sewers. Facilities producing reclaimed water operate under permits issued pursuant to RCW 90.46 and WAC 173-219, which are frequently combined with NPDES or SWD permits for administrative efficiency.  Construction of outfalls and utility crossings in waters of the United States requires Section 401 water quality certification to accompany Corps of Engineers Section 404 or Section 10 permits, with additional local floodplain and shoreline permits potentially applicable, as described in the discussion on alternatives in Chapter 6.

## Operational Requirements

Operational monitoring requirements are specified within NPDES and SWD permits, with laboratory accreditation rules and applicable exceptions detailed in WAC 173-216 [20][7].

## Regulatory Precedence

When regulatory conflicts arise, Water Quality Standards established under WAC 173-201A take precedence and may require effluent limits more stringent than technology-based standards. In cases where multiple requirements apply, facilities must meet the most restrictive standard. For projects receiving Ecology funding, SERP allows SEPA documentation to satisfy NEPA-like requirements, though EPA retains NEPA oversight authority for projects funded through the Water Infrastructure Finance and Innovation Act (WIFIA) program [14][2].

Table 1-1.  Wastewater System Regulatory Framework Summary

| Regulatory Area | Requirements |
| --- | --- |
| Planning | Ecology approval required for general sewer plans, engineering reports, and plans/specs before construction. Content/sequence per WAC 173-240 and Orange Book (CSWD). SEPA review required prior to Ecology approvals. SERP/NEPA applies when federal funding involved |
| Design Standards | Must be reasonably consistent with CSWD. Ecology recognizes WEF, ASCE, APWA, EPA design references. Reclaimed water must follow WAC 173-219 (Purple Book)• Coordination with Ecology/Health required for reclaimed water |
| Permits - Discharge | NPDES: Surface water discharges (Ecology as delegated authority). SWD: Discharges to ground and certain sewer discharge. Can combine NPDES/SWD in single permit |
| Permits - Reclaimed Water | Required under RCW 90.46/WAC 173-219. Often combined with NPDES/SWD permits |
| Permits - Construction | Section 401 certification for outfalls/crossings (pairs with Corps 404/10). Local floodplain/shoreline permits may apply. |
| Monitoring & Labs | Requirements specified in NPDES/SWD permits. Lab accreditation per WAC 173-216. CSO monitoring per CSWD. Reclaimed water monitoring per Purple Book. |
| Regulatory Precedence | Water Quality Standards (WAC 173-201A) govern. May require limits more stringent than technology-based standards. Mixing zones require AKART and must protect uses. Most restrictive requirement applies when conflicts exist. SERP satisfies NEPA-like requirements for Ecology funding• EPA retains NEPA oversight for WIFIA projects |

## Agency Information

The Tekoa Wastewater Treatment Plant, owned and operated by the City of Tekoa, is located at 7241 Lone Pine Road in Tekoa, WA. The facility utilizes a mixed activated sludge treatment process, followed by chlorine disinfection and de-chlorination. Treated effluent is discharged into Hangman Creek (also known as Latah Creek) at approximately river mile 54.3.

Key contact information and specific location details are provided below:

Table 1.2-1. Agency Information

| Information Category | Details |
| --- | --- |
| Facility Contact / Responsible Official | Steven Thomas, Tekoa Public Works / Jessica May-Johnson, Tekoa Public Works N 419 Washington St, Tekoa, WA 99033 Tel: 509-284-3861 tekoapublicworksdept@gmail.com |
| Facility Location (NAD83/WGS84) | 7241 Lone Pine Road, WA 99033 Latitude: 47.227601° N Longitude: 117.083324° W |
| Discharge Location | Hangman Creek (Latah Creek), river mile 54.3 Latitude: 47.227791° N Longitude: 117.082692° W |

Washington State Department of Ecology (Ecology) is the state regulatory agency responsible for issuing the National Pollutant Discharge Elimination System (NPDES) permit, overseeing compliance, administering potential state funding programs, and approving this Facility Plan.

## Issues and Objectives

The City of Tekoa owns and operates the municipal wastewater collection, treatment, and disposal system serving customers within its incorporated limits. Sewage is conveyed through gravity sewer mains converging towards the City's wastewater treatment plant (WWTP) located off Lone Pine Road, on the south bank of Hangman Creek, in northeast Tekoa at 7241 Lone Pine Road on parcel 818000000000007, located at the GPS coordinates listed in Table 1.2-1 above.

Tekoa's wastewater treatment plant utilizes an activated sludge treatment process. Following treatment, which includes chlorine disinfection and de-chlorination, effluent is discharged to Hangman Creek under National Pollutant Discharge Elimination System (NPDES) Permit No. WA0023141.

Tekoa’s WWTP began as a trickling filter system in 1950 and was converted to an activated sludge process in 1974, and has successfully served the community for decades. However, despite various upgrades over time, ongoing assessment and long-term planning remain crucial for the facility's continued effectiveness. A comprehensive sewer plan was completed in 2006, and subsequent efforts have focused on addressing significant operational challenges stemming from significant infiltration and inflow issues.

Since the 2006 general sewer plan, continued upgrades and planning resulting from the system’s persistent performance issues primarily stem from severe infiltration and inflow (I&I) within the aged collection system. Until recently, excessive I&I lead to year-round influent and infiltration flows, impacting treatment efficiency.

The present planning effort aims to establish a foundation for sustained regulatory compliance, particularly in response to recent changes in Total Maximum Daily Load (TMDL) requirements for nutrients and temperature in Hangman Creek discussed in Chapter 2. Addressing community needs and improving overall operational efficiency are also long-term goals. The 2006 sewer plan and subsequent actions have prioritized resolving the I&I issues as a critical step before definitive upgrades to the treatment plant itself can be accurately planned and implemented.

Specific areas identified for past and ongoing evaluation and improvement either by town staff, previous reports, or NPDES permit WA0023141 include:

- Extensive rehabilitation of the collection system to reduce I&I, including pipe and manhole replacements. Evidence of this effort being largely successful in achieving compliance is presented later in this report, though some inflow and infiltration issues remain.

- Optimization, augmentation, or replacement of the existing activated sludge process components once hydraulic loadings are better managed.

- Effective solids management and removal strategies.

- Evaluation of advanced or tertiary treatment processes or land treatment methods may be necessary to meet stringent nutrient limits and further protect Hangman Creek during critical periods.

As a basis for planning for the continued improvements noted above, the following information is presented in Chapters 2 through 4:

- A thorough summary of the necessary background information required to perform a well-informed alternatives analysis specific to the needs of the Tekoa community.

- An evaluation of the condition and capacity of the existing wastewater collection and treatment facilities.

- A determination of the current and projected wastewater flows and loadings for the six- and 20-year planning period.

# DISCHARGE STANDARDS

## Existing Permit

The Tekoa Wastewater Treatment Plant discharges treated wastewater to Hangman Creek under NPDES Permit No. WA0023141, issued by Ecology on April 23, 2014 and was initially effective from June 1, 2014 to May 31, 2019 with an original permit renewal deadline due to Ecology by May 31st, 2018.  At present, the permit is operating under an extension pending reissuance.

## Limits

Effluent quality discharged from the Tekoa Wastewater Treatment Plant is regulated by NPDES Permit No. WA0023141. The final effluent limitations, detailed in Section S1.A of the permit, are summarized in the table below. These limits specify the required performance standards for various parameters, including monthly and weekly averages, daily maximums, and specific removal efficiencies, ensuring compliance and environmental protection.

Table 2.2-1.  NPDES Permit No. WA0023141 Effluent Limits (Outfall #001)

| Parameter | Average Monthly | Average Weekly |
| --- | --- | --- |
| Biochemical Oxygen Demand (5-day) (BOD5) | 30 milligrams/liter (mg/L) 34.5 pounds/day (lbs/day) 85% removal of influent BOD5 | 45 mg/L 51.7 lbs/day |
| Total Suspended Solids (TSS) | 30 milligrams/liter (mg/L) 34.5 pounds/day (lbs/day) 85% removal of influent TSS | 45 mg/L 51.7 lbs/day |
| Parameter | Minimum | Maximum |
| pH | 6.0 S.U. | 9.0 S.U. |

Table 2.2-1.  NPDES Permit No. WA0023141 Effluent Limits Outfall #001 (Continued)

| Parameter | Average Monthly | Maximum Daily |
| --- | --- | --- |
| Total Ammonia (as NH3-N) | 1.3 mg/L | 2.4 mg/L |
| Total Residual Chlorine (WQ-based) | 4 µg/L | 19 µg/L |
| Parameter (Effective 2024) | 7 DAD Maximum |  |
| Temperature 7 day DAD Max | To take effect 2024: June = 18.2º C July = 21.5º C August = 17.7º C |  |

An exhaustive list of effluent limits for the Tekoa’s WWTP is provided in Appendix A for full permit.

## Compliance History

Review of available records indicates the Tekoa WWTP has experienced challenges in consistently meeting its NPDES permit limits. A Notice of Noncompliance was issued by Ecology in March 2016, citing numeric effluent violations for fecal coliform (6), TSS (6), BOD (2), effluent quantity (2) and chlorine (1) from June 2014 to January 2016.  Significant effort prior to the Notice of Noncompliance has been put forward to improve the the plant’s ability to meet its permit limits, though challenges remain.  See Table 2.3-1 for a summary of the facility’s effluent violations from 2022 to 2024 based on wasteload assessments submitted to Ecology by the town.

| Parameter | Limit Value |
| --- | --- |
| Temperature | June: 18.2°C |
|  | July: 21.5°C |
|  | August: 17.7°C |
| Dissolved Inorganic Nitrogen (DIN) | 0.0132 kg/d (0.0291 lbs/d) |
| Total Phosphorus (TP) | 0.00183 kg/d (0.00404 lbs/d) |
| Fecal Coliform | Monthly Geo. Mean: 100 cfu/100 mL |
|  | Weekly Geo. Mean: 200 cfu/100 mL |
|  | Daily Max Load: 3.1 x 109 cfu/day |
| Turbidity (as TSS) | Avg. Monthly: 34.5 lbs/day |
|  | Avg. Weekly: 51.7 lbs/day |

Table 2.3-1. Effluent Monthly Violations

| Parameter | 2022 Violations | 2023 Violations | 2024 Violations | Parameter Total (3 Years) |
| --- | --- | --- | --- | --- |
| Max Flow (gpd) | 4 | 1 | 0 | 5 |
| Fecal Coliform (no./100mL) | 3 | 0 | 3 | 6 |
| TSS (mg/L) | 0 | 0 | 2 | 2 |
| TSS (Lb.) | 1 | 0 | 0 | 1 |
| Total Violations | 8 | 1 | 5 | 14 |

A review of the Discharge Monitoring Report summaries within these assessments reveals the following compliance trends over the past three years (2022-2024).  While BOD and TSS violations were the focus of the 2016 notice, those challenges have been greatly improved as a result of recent projects aimed at reducing excess I&I.  However, recent data (2022-2024) highlights challenges.

Addressing these ongoing compliance issues, particularly the newly effectuated limits on temperature and dissolved oxygen, as well as managing peak flows, are among the drivers for this Facility Plan.

## Watershed Considerations

The Tekoa WWTP discharges treated effluent to Hangman Creek, a tributary within the Spokane River watershed. Water quality in Hangman Creek is a significant consideration due to its status and potential impacts on downstream uses and stream health.  Given the importance of the creek to the ecological health of the watershed, several studies have been conducted by Ecology on the creek’s health, the background of which is important to understand due to its effect on the Tekoa WWTP NPDES permit. The studies and their consequences are summarized in the sections below.

### 2009 Hangman Watershed Water Quality Improvement Report

The Hangman Creek Watershed Water Quality Improvement Report, published in June 2009 by the Washington State Department of Ecology. The impetus for this report stems from Hangman Creek and its tributaries being listed on Washington State's 303(d) list of impaired water bodies due to failing to meet state water quality standards for fecal coliform, temperature, and turbidity. The federal Clean Water Act mandates the development of a Total Maximum Daily Load (TMDL) for each pollutant and water body on this list to identify and clean up polluted waters. Additionally, there was regional interest in reducing Hangman Creek's phosphorus contribution to the Spokane River, as phosphorus loads are associated with suspended sediments and turbidity and contribute to depressed dissolved oxygen levels in the Spokane River and Lake Spokane.

The objectives of this TMDL report were to develop a plan to meet water quality standards for these three pollutants in Hangman Creek and its tributaries. The study involved characterizing fecal coliform bacteria, heat, and suspended sediment loading. Using the results of the study, TMDL allocations for these parameters were set, and an implementation strategy for adhering to the parameters was put forward. Study included reviewing historical data, engaging local agencies, and integrating fieldwork for technical analysis. Implementation objectives focused on community involvement, developing a local plan, and securing technical and financial assistance to meet the updated standards. The study used historical and field data collected by the Spokane County Conservation District (SCCD), Ecology, and other agencies which had been collected over recent decades. For fecal coliform, temperature, and TSS, statistical and modeling methods were used to generate the recommended load allocations

The results indicated widespread water quality issues in the Hangman Creek watershed, but many of the impacts were resulting from sources unrelated to the Tekoa WWTP. For fecal coliform, many areas and tributaries frequently exceeded criteria, primarily due to storm events (runoff Sources of the exceedances were diverse, including livestock access, malfunctioning septic systems, historically inadequate WWTP disinfection (now largely corrected), wildlife, and stormwater runoff. A 72% bacteria load reduction was deemed necessary at the mouth of Hangman Creek during the July-September critical period, with other areas requiring 10% to 85% reductions. Temperature consistently exceeded the 7-day average daily maximum (7DADM) 17.5 degrees Celsius criterion over many reaches of the Creek during the critical June-August period. Current riparian shade was significantly below the "system potential", which is the estimated shade from mature native vegetation under undisturbed conditions. WWTPs discharging during the critical summer months (Tekoa and Spangle) received specific monthly maximum effluent temperature limits, while those discharging to wetlands or with seasonal restrictions were assigned "no discharge" waste load allocations during these months. Turbidity and TSS were identified as long-standing problems, stemming from naturally erosive streambanks and upland soils destabilized by poor infrastructure and agricultural practices. Although TSS and turbidity showed some recent decline, aquatic communities remained poor, with frequent intense events causing lethal or sub-lethal effects on fish. Statistical modeling predicted a significant reduction in adverse markers if "full protection scenario" (for instance, conservation agriculture, riparian buffers, streambank erosion control) were implemented. WWTPs were considered insignificant sources of TSS, though the watershed’s conditions as characterized in the report are important for understanding the regulatory environment moving forward.

The report issued several key recommendations for water quality improvement. A Water Quality Implementation Plan (WQIP) was to be developed within one year of TMDL approval (see section 2.4.3 for the improvement plan published in 2011), detailing specific actions. Most of the plan’s recommendations focus on nonpoint source pollution and integrate Best Management Practices (BMPs) that reduce erosion, runoff, and livestock impacts, and increase stream shading. However, the report also recommends enforcing stringent effluent limits for Tekoa WWTP. For temperature, ongoing temperature monitoring was required for all WWTPs to refine effluent limits, and permit holders were advised to evaluate their systems to prevent thermal impacts.

### 2011 Hangman Creek Watershed Fecal Coliform, Temperature, and Turbidity TMDL Water Data Summary Report

The "Hangman Creek Watershed Dissolved Oxygen, pH, and Nutrients Total Maximum Daily Load (TMDL) Study Data Summary Report" outlines the foundational data collection for a comprehensive water quality assessment. The impetus for this study arose because previous TMDL evaluations for Hangman Creek, which addressed fecal coliform bacteria, temperature, and turbidity, lacked sufficient data to assess the role of phosphorus in pH and dissolved oxygen (DO) criteria violations. Furthermore, several segments of Hangman Creek and its tributaries were identified on Washington State's 303(d) list of impaired waters for not meeting state water quality standards for pH and DO, necessitating this data collection effort to fill those gaps. The watershed, covering nearly 700 square miles and primarily characterized by dryland farming. The objectives of the study were to refine the existing landscape model of the Hangman Creek watershed and to develop a numerical water quality model for DO and pH analysis, specifically targeting the low-flow summer period using data from collected surveys.

The methodology involved the Washington State Department of Ecology collecting water quality and streamflow data from September 2008 through September 2009. Data collection encompassed synoptic surveys during the summer and fall low-flow seasons, including time-of-travel tests, pH and DO monitoring, and productivity monitoring. The study also monitored nutrient and chemical reference conditions across the watershed's four ecoregions and assessed Washington/Idaho border nutrient loads. Field data collected included pH, conductivity, dissolved oxygen, temperature, and flow. Laboratory analyses were performed for chloride, total suspended solids, alkalinity, various nitrogen and phosphorus species, total organic carbon, dissolved organic carbon, biochemical oxygen demand, chlorophyll, and volatile organic matter. Data collection adhered to the Hangman Creek Watershed Dissolved Oxygen and pH Quality Assurance Project Plan and Ecology's standard collection procedures. The analytical framework for the report focused on summarizing the collected data and performing a quality control and quality assurance analysis. The data presented in the report were intended to comprise part of an ongoing detailed analysis, including water quality modeling and statistical analysis, which were used to establish pollutant load and waste load allocations for Hangman Creek and its tributaries.

The results of this data summary report consist of all collected field measurements, comprehensive laboratory data, continuous temperature plots, streamflow measurements. Because the report was an accounting of a data collection and reporting effort, recommendations are not provided in this "Data Summary Report".

### 2011 Hangman Creek Watershed Fecal Coliform, Temperature, and Turbidity TMDL Implementation Plan

The Hangman (Latah) Creek Watershed Fecal Coliform Bacteria, Temperature, and Turbidity Total Maximum Daily Load (TMDL) Water Quality Implementation Plan outlines a comprehensive strategy to restore water quality in the Hangman Creek Watershed. The impetus for this plan stems arose from the fact that streams within the Hangman Creek Watershed were shown to be significantly impaired by excess fecal coliform, turbidity, and elevated water temperatures. The primary objective of this Water Quality Implementation Plan was to expand upon the recommendations of the preceding TMDL report by detailing the roles and responsibilities required to bring the impaired streams into compliance with water quality standards for bacteria, temperature, and turbidity. Additionally, the plan recommend activities that will reduce nutrient contributions, particularly phosphorus, which is a significant concern for the Spokane River and Lake Spokane Dissolved Oxygen TMDL (to which Hangman Creek is a tributary), and is also linked to dissolved oxygen and pH impairments in Hangman Creek.

As previously touched upon, the analytical framework for this plan is based on the Total Maximum Daily Load (TMDL) approach, mandated by the federal Clean Water Act (CWA) for all 303(d) listed impaired waters. A TMDL is a quantitative assessment that determines the maximum amount of a pollutant a water body can receive without violating water quality standards (the "loading capacity") and then allocates this load among various sources. This allocation includes wasteload allocations (WLAs) for discrete point sources (like municipal or industrial discharge pipes) and load allocations (LAs) for diffuse nonpoint sources (such as agricultural or urban runoff). The report outlines a an implementation strategy, expanding on the pollutant reduction requirements and allocations established in the initial TMDL document approved in 2009. Town of Tekoa Wastewater Treatment Plant (WWTP) - Regulatory Compliance and Water Quality Implementation

The Town of Tekoa Wastewater Treatment Plant (WWTP), one of six National Pollutant Discharge Elimination System (NPDES) permitted facilities discharging to surface waters within the Hangman Creek Watershed, plays a specific role in the comprehensive Water Quality Implementation Plan. Its effluent discharges directly into Hangman Creek. For fecal coliform bacteria, the TMDL assessment identified the Tekoa WWTP as the only point source requiring a reduction from its then-current NPDES permit limits. The TMDL established a specific 78% reduction target for Tekoa WWTP to achieve a wasteload allocation, down from a previously calculated load which was based on 2003-2004 data. However, the report also notes that, based on the most recent monitoring records at the time of publication, the Tekoa WWTP was already in compliance with this fecal coliform target reduction.  This has by-in-large remained true in the intervening years outside a sparse set of violations.

Of key importance to operation of any propose wastewater treatment facility, the Tekoa WWTP faces specific numeric wasteload with respect to temperature allocations for effluent discharge during the critical summer months of June, July, and August. These WLAs specify maximum effluent temperatures of 18.2°C for June, 21.5°C for July, and 17.7°C for August. This is a distinct requirement, as several other WWTPs in the watershed have a "No discharge" requirement during these months. Furthermore, the Hangman Creek reach above the Tekoa WWTP has a significant need for riparian restoration, requiring a 50% increase in effective shade to reach system potential vegetation, indicating existing temperature challenges in the surrounding stream environment.

For TSS, the report states that the current NPDES turbidity limits for all WWTPs, including Tekoa, are considered adequate to protect water quality and require no further reduction. Overall, as with other WWTPs in the watershed, when the NPDES permit for the Town of Tekoa WWTP is reissued, it will contain the wasteload allocations established in this TMDL. The Town is encouraged to work closely with its Ecology permit manager to ensure all necessary actions are addressed in its monitoring and permit requirements for TMDL compliance. Additionally, the Town of Tekoa, like other towns in the watershed, is advised to plan for necessary improvements to meet these limits and to prepare for potential nutrient limits in the future when its permits are reissued, as nutrient reduction is a broader goal related to the Spokane River and Lake Spokane Dissolved Oxygen TMDL.

### 2020 Tekoa Wastewater Treatment Plant Dissolved Oxygen, pH, and Nutrients Receiving Water Study

The Tekoa Wastewater Treatment Plant Dissolved Oxygen, pH, and Nutrients Receiving Water Study was primarily driven by the aging infrastructure of the City of Tekoa's wastewater treatment plant (WWTP), which was originally built in 1950 with significant upgrades in 1974 and 1990. Further impetus was the plant's compliance schedule to meet effluent temperature limits by July 2024, as established by the 2009 Hangman Creek Watershed TMDL. Crucially, preliminary data from 2009 had indicated that nutrient discharges from the Tekoa WWTP might be contributing to DO and pH impairments in Hangman Creek. The objectives of the 2017 field study, which focused on nutrients, pH, dissolved oxygen, and algal eutrophication during May-October critical period, were to determine the effluent nutrient load limits necessary to protect pH and DO in Hangman Creek and to provide essential information for Tekoa's facility planning efforts. The study aimed to present its field investigation findings, offer a modeling analysis of effluent nutrient impacts, and recommend specific effluent nutrient limits.

The analytical approach for study initially planned to use existing models standard for river water quality, which successfully calibrated hydrodynamics and temperature. The results of the study revealed several key findings which revealed consistent impacts on pH and DO were observed downstream of Tekoa WWTP during summer low-flow periods, with pH frequently exceeding the water quality standard. Unlike many small streams, suspended algae played a crucial role in determining summertime pH and DO levels in upper Hangman Creek, attributed to the exceptionally slow water movement through deep, wide pools. Tekoa WWTP was identified as the predominant source of soluble reactive phosphorus and contributed the majority (at times over 90%) of both SRP and dissolved inorganic nitrogen (DIN) during the critical low-flow period. Algae growth was primarily nitrogen-limited, though phosphorus was also found to be co-limiting. Environmental factors like extreme seasonal streamflow variability (effluent from the Tekoa plant comprised up to 10-15% of downstream flow during summer), clear water allowing light penetration, and warm summer temperatures created a critical season for nutrient-driven algal growth and subsequent pH and DO impacts.

Based on these findings, the study offered several recommendations to Ecology to implement stringent effluent nutrient load limits for the Tekoa WWTP for DIN and TP. These limits are recommended to be applied annually during the critical season from June through October, as determined by flow and temperature conditions.  Of note about these recommendations is their relative severity:  according to XXX tolerances, the recommendations are outside of measurable limits and are expected to be very hard to achieve without expensive, specialized equipment.

### Summary and Implications

The series of studies conducted on the Tekoa Wastewater Treatment Plant (WWTP) and the broader Hangman Creek watershed have profound relevance to the feasibility proposed plant modifications, revealing critical environmental challenges and leading to stringent regulatory requirements.

This extensive body of research should critically inform the planning for a new wastewater treatment plant for the City of Tekoa, especially given the existing facility's aging infrastructure and urgent need for repair, upgrade, or replacement. The new plant must be designed to meet the highly restrictive effluent nutrient load limits for dissolved inorganic nitrogen (DIN) and total phosphorus (TP), which are applicable annually during the critical season from June through October. These limits represent a small fraction of current nutrient discharges, and meeting the proposed limits will necessitate either advanced treatment technologies or periods of diverted effluent flow such as land application or seasonal storage. Furthermore, the new facility must comply with the effluent temperature limits established by the 2009 TMDL which were brought into effect in July 2024. Options for thermal reduction such as seasonal storage, land application, or infiltration trenches should be thoroughly investigated. Planned modifications must accommodate the poor dilution factor of Tekoa's effluent in Hangman Creek during summer low flows, where wastewater can comprise up to 10-15% of the downstream flow.

# BACKGROUND INFORMATION

This section provides context regarding the environmental setting, community characteristics, and population trends relevant to the Tekoa WWTP Facility Plan.

## Environmental

### Wetlands

#### Existing conditions

A desktop review of available mapping resources, including the City of Tekoa Critical Areas Data Maps maintained per TMC 4.24.100 (available at the City Clerk’s office) and the National Wetlands Inventory (NWI), indicates that the Tekoa has a defined procedure to consider construction of facilities that may be within the City’s Critical Areas Overlay Zone, which includes all areas within 250 feet of designated wetlands and critical wildlife habitat, aquifer recharge areas, geologically hazardous areas (with a 25-foot buffer), and frequently flooded areas mapped as FEMA Zone A or AE (TMC 4.24.010, 4.24.100). The data is available in Appendix X of this report, and should be considered illustrative and non-regulatory. they are intended to alert applicants to potential constraints and to trigger site-specific analysis (TMC 4.24.100). Confirmation of wetland presence, extent, and type requires a formal field delineation by a qualified professional using an acceptable methodology and applying the Washington Department of Ecology’s wetland methods. Following delineation, each wetland must be rated using the Eastern Washington wetland rating system as adopted by the City (Washington State Wetland Rating System for Eastern Washington; Ecology Publication 04-06-015, or as updated) to determine category, functions, and special characteristics (TMC 4.24.050.A–B). Surveyed boundaries and ratings will supersede planning-level mapping and will be used to set regulatory buffers and to inform siting and layout of the preferred alternative.

#### Regulatory setting

Wetlands are designated critical areas in the City of Tekoa and are regulated under Tekoa Municipal Code (TMC) Chapter 4.24, Protection of Critical Areas. Any development proposed within the Critical Areas Overlay Zone is subject to project review unless specifically exempt. Where projects are likely to affect critical areas, applicants must submit a technical study prepared by qualified professionals using best available science to identify precise limits and impacts. Wetlands must be delineated and rated using Ecology’s Eastern Washington wetland rating system, and standard wetland buffers are established by local code as follows (TMC 4.24.050.C):

| Wetland Category | Buffer Required |
| --- | --- |
| Category I | 250 feet |
| Category II | 200 feet |
| Category III | 150 feet |
| Category IV | 50 feet |

Buffers may be increased case by case basis, based on best available science, or decreased by up to fifty percent if stringent findings are met. Certain low-impact uses may occur within buffers if they do not degrade wetland functions. The City applies mitigation sequencing that requires projects to first avoid impacts, then minimize, rectify, reduce over time, compensate, and monito. If unavoidable wetland or buffer impacts occur, a mitigation or enhancement plan prepared by a qualified expert is required and must follow Department of Ecology guidance. Frequently flooded areas are regulated under the City’s flood damage prevention ordinance using FEMA FIRMs, and aquifer protection standards apply within critical aquifer recharge areas. SEPA applies to the project per state law and is administered by the City. The need for shoreline permits depends on whether the site lies within shoreline jurisdiction under the City’s SMP, which must be confirmed.

#### Alternatives analysis

At the planning stage, site and layout alternatives should be screened against criteria informed by Ecology guidance and the local regulatory framework. Alternatives that avoid wetlands and their buffers are preferred. Where complete avoidance is not practicable, layouts that minimize new crossings, grading, and encroachments within buffers were favored. Concepts were also evaluated for compatibility with maintaining wetland hydrology and water quality through stormwater management consistent with the locally adopted stormwater manual. Finally, the screening considered each alternative’s potential to reduce the need for compensatory mitigation.

#### Permitting

Based on planning-level information, wetland-related approvals for the preferred alternative are expected to include local critical areas review and permitting under the City of Tekoa’s CAO and SEPA review led by Ecology. Ecology’s facility planning and design approvals under will be integrated with siting and environmental protection measures. If the project is within shoreline jurisdiction or affects associated wetlands, shoreline permits under the City of Tekoa’s Shoreline Master Program may be required. Federal and state water quality approvals depend on final design: if discharge of dredged or fill material to wetlands or other waters is proposed, a Clean Water Act Section 404 authorization from the U.S. Army Corps of Engineers and a Section 401 Water Quality Certification from Ecology will be required; if no such discharge is proposed, 404/401 may not apply. Construction-phase stormwater permitting under Ecology’s Construction Stormwater General Permit will be confirmed based on the area of disturbance. If any work extends below the ordinary high water mark of, Hydraulic Project Approval from the Washington Department of Fish and Wildlife may also be needed. Final permit triggers and sequencing will be confirmed after a conceptual layout establishes whether wetland or buffer impacts are proposed.

#### Anticipated Mitigation strategy

If unavoidable wetland or buffer impacts remain after applying avoidance and minimization, compensatory mitigation will be developed in accordance with Ecology’s guidance, with a preference for a watershed-based approach when feasible. Detailed mitigation elements, including selection of mitigation type and location (on-site, off-site, mitigation bank, or in-lieu fee), preliminary ratio assumptions consistent with the local CAO/SMP (to include performance standards, monitoring, and long-term protection) will be determined after the delineation and rating are complete and in coordination with permitting agencies. A planning-level scan of potential mitigation options will be conducted for each alternative presented to identify opportunities within the watershed and to confirm availability of any applicable wetland mitigation banks or in-lieu fee programs. The mitigation strategy will be refined alongside the preferred alternative layout to ensure consistency with local code, Ecology guidance, and the “no net loss” standard where shoreline jurisdiction applies.

<<Figure 3-2.  Tekoa Wetlands Map>>

### Shoreline

Hangman Creek is subject to the Washington State Shoreline Management Act (SMA).  A summary of the City’s Shoreline Management Plan was published in 2024, and its implications to this feasibility study are summarized below:

City of Tekoa's Shoreline Master Program (SMP)

The City of Tekoa's Shoreline Master Program (SMP) is a document that aligns the City’s shoreline policy with the Washington State Shoreline Management Act (SMA). Its primary goal is to provide a balanced use of the City’s shoreline by integrating environmental protection, public access, and water-oriented development. The SMP covers Latah Creek, land within 200 feet of the ordinary high water mark (OHWM), floodways, contiguous 100-year floodplains extending 200 feet inland of a floodway, and associated wetlands.

Core principles of the SMP include:

- Environmental Protection: Safeguarding natural resources like land, vegetation, wildlife, and aquatic life.

- Public Access: Preserving and enhancing opportunities for the public to enjoy shorelines.

- Water-Oriented Uses: Prioritizing uses that are water-dependent, water-related, or water-enjoyment.

- No Net Loss of Ecological Functions: A central tenet requiring all uses and developments to maintain the current aggregate total of shoreline ecological functions, with impacts identified and addressed.

The SMP is structured to define its purpose, vision, shoreline jurisdiction and five environment designations (Urban Conservancy, Shoreline Residential, Shoreline Parks, High Intensity, and Aquatic), general policies, specific use and modification policies, and administrative procedures. Each environment designation has specific management policies and use preferences. A key regulatory tool is the "Shoreline Use and Modification Table" which classifies activities as permitted, conditional, or prohibited within each designation.

Project Impacts for Wastewater Treatment Plant

The planning and construction of a new wastewater treatment plant (WWTP) within the City of Tekoa's shoreline jurisdiction are subject to a rigorous regulatory process which relate to the City’s SMP, significantly impacting the project's timeline, feasibility, and costs.  Those impacts are summarized in the table below, the aim of which is to help City officials consider the impact of siting and proposed WWTP improvements near the creek’s designated shoreline:

| Requirement | Description / Specific Requirement | SMP Reference |
| --- | --- | --- |
| Permit Type | Requires a Shoreline Conditional Use Permit (SCUP) in all shoreline environment designations. | Table 4.10-1 |
| Siting Preference | Prohibited unless no other feasible nonwater-oriented option is available. | 5.10.B.4 |
| SCUP Approval Criteria | Must demonstrate consistency with SMA/SMP, no public use interference, compatibility with other uses, no significant adverse environmental effects, no detrimental public interest, and consideration of cumulative impacts. | [7.6.G.4, 7.6.G.5] |
| "No Net Loss" Principle | Must achieve no net loss of shoreline ecological functions through design, location, size, construction, and maintenance. | [4.3.B.1] |
| Mitigation Sequencing | Required for SCUPs; mandates a sequence: avoid, minimize, rectify, reduce, compensate, then monitor impacts. | [4.3.B.3.b, 4.3.B.4] |
| Mitigation Plan | Unavoidable impacts need a plan by a qualified professional, including inventory, management, drawings, specifications, a minimum three-year maintenance/monitoring, and contingency. | [4.3.B.6, 4.3.B.6.e] |
| Critical Areas Report | If in/adjacent to critical areas, a detailed report by qualified professionals is required, assessing impacts, alternatives (including "no development"), and proposed mitigation. | [Appendix B 2.D.2] |
| Water Quality & Stormwater | Must use BMPs to maintain water quality/quantity, ensure "no net loss," prohibit hazardous discharges, require spill prevention, and use approved water-contact materials. | [4.5.B.1, 4.5.B.3, 4.5.B.4, 4.5.B.5, 4.5.B.6, 4.5.A.2] |
| Flood Hazard Management | Avoid new structural flood measures in CMZ/floodway. Public utilities may be allowed if no feasible alternative or disproportionate cost (>20%), with mitigation, and scientific/engineering analysis. | [4.6.B.5, 4.6.B.3.d, 4.6.B.6.a, Footnote 1, 111] |
| Shoreline Vegetation Conservation | Conserve upland/waterward vegetation. Clearing must be minimal, using mitigation sequencing. Removal of native or slope-stabilizing non-native vegetation requires mitigation. | [4.4.A.1, 4.4.B.4, 4.4.B.5] |
| Public Access | Public access may be required for SCUPs, unless exempted (for instance, safety, security, disproportionate cost). Must ensure "no net loss" of ecological function; water-dependent uses and public access have priority over views. | [4.8.B.4, 4.8.B.5, 4.8.B.10, 4.2.B.5] |
| Height Limitations | General 35-foot height limit. Utilities (for instance, sewage treatment plants) may exceed if demonstrated necessary, minimized, and not obstructing public views/interest. | [4.2.B.3, 4.11.C] |
| Timeline Impacts | SCUPs involve City Council and Ecology review, causing significant delays. Pre-application studies and a minimum five-year mitigation monitoring period further extend the timeline. | [7.6.G.1, 7.2.A.5, 7.2.C.2.a, 4.3.B.6.e, Appendix B 2.F.4.d, Appendix B 2.J.7, 7.6.I] |
| Feasibility & Cost Impacts | Higher costs from strict design, engineering, construction, mitigation (restoration, monitoring), and limited siting options for non-water-oriented use. | [5.10.B.4, 4.3.B.6, 4.4.B.5, 4.6.B.3.d, Footnote 1, 111] |

### Endangered Species/Habitat

The USFWS Information for Planning and Consultation tool for the project area (which includes both the lift station site and proposed land application areas) includes the following species:

Table 3.1-1.  USFWS Affected Species List

| Category | Species | Status |
| --- | --- | --- |
| Birds | Yellow-billed Cuckoo | Threatened |
| Fishes | Bull Trout | Threatened |
| Insects | Monarch Butterfly | Proposed Threatened |
|  | Cuckoo Bumble Bee | Proposed Endangered |
| Flowering Plants | Spalding’s Catchfly | Threatened |

### National Wild and Scenic Rivers Act

Hangman Creek has not been given a designation under the National Wild and Scenic Rivers Act.

### Archeological and Historical

Recent projects have served as opportunities for archeological and historical review of the treatment plant site and facilities nearby.  Most recently, a cultural survey was carried out in preparation for the construction of the influent lift station.  The primary goal of the cultural resource survey was to identify and assess any archaeological or cultural resources within the proposed construction area of the influent lift station. This survey was undertaken to fulfill the cultural resources regulatory requirements mandated by the Department of Ecology and the Spokane Tribal Historic Preservation Office before beginning construction activities.

The search revealed four previously recorded historic properties within a 1-mile radius of the project area, primarily consisting of railroad-related features. The subsurface survey of the area yielded no pre-contact archaeological materials. However, one historic artifact, a 4-inch nail, was found in one STP, and modern debris (concrete fragments) was recovered from another. The soil profile generally indicated disturbed conditions, likely from the initial construction of the wastewater treatment plant.

The Spokane Tribe of Indians Preservation Program concluded that the proposed project was unlikely to have adverse effects on significant cultural resources based on the survey findings. However, due to the treatment plant’s proximity to Hangman Creek and (and the Creek’s cultural importance), the possibility of encountering cultural materials during construction was emphasized and remains important. The primary recommendation was to have an Inadvertent Discovery Plan (IDP) in place before any ground-disturbing activities began.

## Land Use and Zoning

(WAC 173-240-050 (d)(i))

Land use and zoning patterns within the wastewater service area are fundamental considerations for facility planning as they dictate the type, density, and location of existing and future development. See Figure 3.3-1 for a map illustrating the current zoning designations in Tekoa below.

Insert Zoning Map

Table 3-1 Tekoa Zoning and Density Summary

| Zone | Abbreviation | Total Zone Area | Minimum Lot Size (Sq. Feet) | Standard Max Density1 (Dwellings / Sq. Feet) |
| --- | --- | --- | --- | --- |
| Rural Residential | RR |  | 10,000 | 1 per 10,000 |
| Urban Residential | UR |  | 5,000 | 1 per 5,000 |
| Commercial | C |  | 5,000 | 1 per 5,000 |
| Industrial | I |  | NA | NA |
| Mobile Home Park (Overlay District) | MHP |  | 15,000 | 5.36 per 15,000 |

  - For full density policy, see the City of Tekoa municipal code.  Densities found in Table 3-1 are for general information and reference purposes only. Standard max density represents normal use and does not fully describe specifics of the policy such as d

Rural Residential (RR), Urban Residential (UR), Commercial (C), and Industrial (I). As Tekoa grows, zoning may change, affecting both population density and development patterns, which will influence wastewater demand.

The purpose of conducting growth projections in a wastewater facility plan is to accurately estimate future wastewater flows and loads, ensuring that the wastewater collection, treatment, and disposal facilities are adequately sized to meet projected demands over the planning period. Zoning is considered in wastewater management planning because it dictates the types and density of development allowed in different areas. This directly impacts population density, water usage patterns, and consequently, the volume and character of wastewater generated. By analyzing existing zoning and anticipated changes in local land use plans, future wastewater demands can be projected more accurately across the service area and be used as an aid for planning infrastructure maintenance and improvements.

This Facility Plan covers the period from 2025 to 2045 and is intended to align with the community's comprehensive planning updates and capital improvement cycles. This facility plan considers several growth scenarios for projecting future wastewater needs. See Section 3.7 for population projections.

## Urban Growth Areas and Future Development Trends

(WAC 173-240-050 (d)(i))

This facility plan utilizes growth scenarios to project wastewater needs over specific planning periods: a 6-year near-term period from 2024 to 2030 and a 20-year long-term period from 2025 to 2045. This dual timeframe allows for both immediate planning and long-range infrastructure needs assessment, accommodating both known near-term projects and longer-term build-out potential. The Growth Management Act (GMA) is a series of statutes that require state and local governments to manage growth by planning and protecting critical areas and designating urban growth areas where development is concentrated. GMA planning significantly influences wastewater treatment facility planning by directing where future wastewater service will be needed and promoting efficient infrastructure investment within designated areas.

## Tekoa Area Geography and Landscape

(WAC 173-240-050(f))

Tekoa is in an agricultural area of Eastern Washington known as the Palouse. It is situated approximately 40 miles southeast of Spokane.  The area surrounding Tekoa is characterized by characteristic rolling hills of the Palouse region. The primary industry related to the area's geography is agriculture. The geography, particularly the terrain and presence of Hangman Creek and Little Hangman Creek, influences local drainage patterns which are relevant to stormwater management and potential infiltration/inflow into the sewer system.

The area soils are predominantly silt or loess, which accumulated from glacial deposits overlying the area’s basalt flow formations, along with the siltstones and sandstones of the Latah Formation. Buttes such as Tekoa Mountain, formed from islands of siltite and quartzite jutting above the basalt flows, are composed of harder, less permeable rock; these features generally lead to lower water infiltration rates, increased surface runoff, and the development of thin, rocky soils often unsuitable for agriculture. Understanding the areas geological setting and the soil types and underlying that geology is important for evaluating infiltration potential and site suitability for infrastructure construction related to treatment.

## Tekoa Water System Description

The City of Tekoa owns and operates a Group A public water system (DOH ID: 828707) that serves the residents within the city limits. The system includes 3 active wells, 1 Irrigation well, 1 decommissioned well, 1 storage reservoirs, and a network of distribution and transmission mains. The system operates with a single pressure zone.

### Water Sources

The City’s water supply comes from two chlorinated ground water wells, both with vertical shaft turbine pumps and shelters. There is an also an irrigation well at the golf course and a decommissioned well as part of the City’s water system.

- Well 1 (AGG-171) or the “North Well” across from city hall at 400 Washington St was an original well for the city built in the late 1920’s – early 1930’s. It was decommissioned in 2011 after a partial collapse. It was a 6” Diameter, 176ft deep well producing 210 gallons per minute (gpm).

- Well 2 (AGG-172) or the “South Well” across from city hall at 400 Washington St was an original well for the city built in the late 1920’s-1930’s was decommissioned in 2009. It was a 4” diameter, 167ft deep well producing 100 gpm

- Well 3 (AGG-173) or the “Truax Well” at 402 Line St at the corner of Truax St and Line St serves as the City’s primary Well. It was built in 1978. It is a 16” diameter 1400ft deep well producing 900 gpm.

- Well 4 (AAU-279) constructed in 2006 is located at the city’s golf course at 202 Golf course Rd and serves as an irrigation well for the City’s golf course. It is an 8” diameter 180ft deep well producing 100 gpm.

- Well 5 (APS-592) is across from City Hall at 400 400 Washington St was constructed in 2011 and commissioned in 2012. This well was drilled adjacent to AGG-171 and, replacing it and well AGG-172. This well is used as the City’s backup/emergency well It is a 12” diameter 303ft deep well producing 280 gpm.

All active wells are in the Columbia River Basalt Group aquifer system providing a source of high-quality groundwater with minimal treatment requirements beyond chlorination for disinfection.

### Water Storage

The water system includes 1 in ground concrete reservoir situated on the hillside about a half mile north of City Hall at the end of Carbury Rd. It has a capacity of <##,###> gallons. This reservoir was originally constructed in 19## and was rehabilitated as part of the towns 2011 water project???  This stored capacity supports both operational supply and fire flow demands. Water is conveyed from the reservoir to the rest of the distribution system via a 16-inch PVC transmission main connecting to the rest of the system at the intersection of Alder and Washington.

### Distribution System

The distribution system consists of cast iron, ductile iron, and PVC pipes ranging in size from 4 inches to 16inches with the majority being 8-inch PVC installed as part of the Towns 2011 water project. The system consists of 23,050 feet of water distribution mains, fire hydrants, valves and service connections. As of the latest count, the system has 456 metered connections including residential, commercial, and irrigation users, with no unmetered connections.

The water system serving

### Water Sources

## Population Growth and Projections

The Tekoa wastewater facilities plan must account for future growth based on reliable population projections. Using a population projection that aligns with regional trends ensures that the planned system and facilities improvements are appropriate for the projected demand without being overbuilt (resulting in unnecessary capital costs) or inadequate (resulting in capacity shortfalls). The following population projections include five-year progress reporting cycle to allow officials to reassess capacity needs and funding allocations based on actual population trends.

### Population Data Sources

The population data used to make the projections are drawn from four data sets:

- The Washington State Office of Financial Management’s (WAOFM) decennial census series from 1890-2020

- WAOFM Growth Management Act (GMA) Population Projections (2022)

- WAOFM’s April first postcensal estimates from 1960-2024, and

- The National Historic Geographic Information System’s census tract population data for 1970-2020.

### Demographic and Housing Analysis (2014-2024)

Over the decade from 2014 to 2024, Tekoa’s population saw a modest 4% increase from 788 in 2014 to 820 in 2024 based on WA OFM’s Intercensal population data.  Over that same time frame Tekoa built an additional 10 housing units, going from an estimated 359 units in 2014 to 369 units in 2024, a 2.78% Increase. This means that Tekoa’s average household size increased by 0.65% from 2.37 residents/household in 2014 to 2.39 residents/household in 2024.

From 1980 to 2024 the City of Tekoa has declined in population and expanded in land area. In 1980 the population was 854 over a land area of 1.00 square miles. In 2024 the population is 820 over a land area of 1.23 square miles. This expansion in land area reflects annexations or boundary adjustments. The population density, which is the number of people per square mile, has fluctuated because of these changes. In 1980 the population density was 854 people per square mile, and it decreased to 669 people per square mile in 2024.

Table 3.7-A. Tekoa—Key Metrics (2014 vs 2024)

| Metric | 2014 |  | 2024 | Change |
| --- | --- | --- | --- | --- |
| Population | 788 | 820 |  | +4.1% |
| Housing Units | 359 | 369 |  | +2.8% |
| Occupied Units | 310 | 322 |  | +3.9% |
| Occupancy Rate | 86.4% | 87.3% |  | +0.9 pp |
| Avg. Household Size | 2.37 | 2.39 |  | +0.02 |
| City Area (mi²) | 1.00 | 1.23 |  | +23% |
| Density (persons/mi²) | ~854 | ~667 |  | −22% |

Table 3.6-1: Tekoa Annual Population and Housing WAOFM Data (2014-2024)

| Category | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total Population | 788 | 808 | 808 | 802 | 810 | 810 | 817 | 810 | 810 | 805 | 820 |
| Household Population | 735 | 759 | 755 | 751 | 762 | 765 | 766 | 759 | 759 | 755 | 769 |
| Group Quarters Population | 53 | 49 | 53 | 51 | 48 | 45 | 51 | 51 | 51 | 50 | 51 |
| Total Housing Units | 359 | 364 | 364 | 361 | 364 | 364 | 366 | 366 | 366 | 363 | 369 |
| Occupied Housing Units | 310 | 320 | 318 | 316 | 320 | 321 | 321 | 318 | 318 | 316 | 322 |
| Occupancy Rate (%) | 86.36 | 87.91 | 84.36 | 87.53 | 87.91 | 88.19 | 87.70 | 86.95 | 86.95 | 87.13 | 87.31 |
| Average Household Size | 2.37 | 2.37 | 2.37 | 2.38 | 2.38 | 2.38 | 2.38 | 2.39 | 2.39 | 2.39 | 2.39 |

### Comparison of Demographic and Housing Trends: Whitman County Vs. Tekoa

Whitman County and Tekoa exhibit some key demographic and housing similarities, but also some notable differences. Over the decade from 2014 to 2024, Whitman County’s population grew slightly more than Tekoa, increasing by 6.4% from 45,817 residents in 2014 to 48,750 in 2024 based on the intercensal data from WA OFM. However, if the City of Pullman is excluded from this data, Rural Whitman County saw a much smaller population increase of only 0.73% from 14,959 residents in 2014 to 15,070 residents in 2024.

Both areas saw increases in housing stock during this period, with Whitman County’s total housing units increasing by 12% to 22,257 units in 2024 compared to just 19,870 units in 2014. However, Pullman again made up most of the increase with Rural Whitman County seeing a decrease of 0.13% in its housing stock from 7,315 units in 2014 to 7,305 units in 2024

Table 3.7-1: Whitman County Annual Population and Housing OFM Data (2014-2024)

| Category | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total Population | 45,817 | 46,380 | 46,623 | 14,983 | 15,027 | 46,961 | 47,217 | 47,871 | 47,973 | 44,600 | 47,800 |
| Household Population | 39,773 | 39,928 | 40,430 | 40,925 | 41,079 | 41,317 | 41,455 | 38,540 | 41,306 | 41,565 | 42,126 |
| Group Quarters Population | 6,044 | 6,452 | 6,193 | 6,036 | 6,138 | 6,554 | 6,518 | 6,025 | 6,428 | 6,469 | 6,555 |
| Total Housing Units | 19,870 | 20,195 | 20,309 | 20,540 | 20,586 | 20,775 | 20,922 | 21,629 | 21,739 | 21,837 | 22,257 |
| Occupied Housing Units | 17,890 | 17,958 | 18,187 | 18,412 | 18,479 | 18,587 | 18,650 | 17,339 | 18,583 | 18,699 | 18,952 |
| Occupancy Rate (%) | 90.07 | 88.92 | 89.55 | 89.64 | 89.76 | 89.47 | 89.17 | 80.16 | 85.48 | 85.63 | 85.15 |
| Average Household Size | 2.2232 | 2.2234 | 2.2230 | 2.2227 | 2.2230 | 2.2229 | 2.2228 | 2.2228 | 2.2228 | 2.2228 | 2.2228 |

Table 3-2.7-2: Rural Whitman County Annual Population and Housing OFM Data (2014-2024)

| Category | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total Population | 14,959 | 15,007 | 14,995 | 14,983 | 15,027 | 15,060 | 15,072 | 14,910 | 15,010 | 15,040 | 15,070 |
| Household Population | 14,837 | 14,880 | 14,871 | 14,849 | 14,889 | 14,937 | 14,939 | 14,612 | 14,879 | 14,921 | 14,983 |
| Group Quarters Population | 122 | 127 | 124 | 134 | 138 | 123 | 133 | 331 | 196 | 185 | 155 |
| Total Housing Units | 7,315 | 7,312 | 7,302 | 7,281 | 7,280 | 7,286 | 7,277 | 7,224 | 7,269 | 7,295 | 7,305 |
| Occupied Housing Units | 6,434 | 6,450 | 6,444 | 6,431 | 6,445 | 6,465 | 6,465 | 6,343 | 6,439 | 6,455 | 6,479 |
| Occupancy Rate (%) | 87.96 | 88.21 | 88.25 | 88.33 | 88.53 | 88.73 | 88.84 | 87.80 | 88.58 | 88.49 | 88.69 |
| Average Household Size | 2.0283 | 2.0350 | 2.0366 | 2.0394 | 2.0452 | 2.0501 | 2.0529 | 2.0227 | 2.0469 | 2.0453 | 2.0510 |

### Comparison of Demographic and Housing Trends: Spokane County Vs. Tekoa

As Tekoa sits just 4.5 miles south of the Spokane/Whitman County line on SR-27, it was determined that Spokane County’s population trends should also be considered as part of the population projection. Spokane County and Tekoa also exhibit key demographic and housing similarities but do have some bigger differences than Whitman County and Tekoa do. In 2014 WAOFM’s intercensal population estimate for Spokane County was 489,986 and increased by 14.16% to 559,400 in the 2024 postcensal estimate from WAOFM. Excluding the Spokane Municipal Statistical area, this increases to a 16.25% increase from 163,207 in 2014 to 189,735 in 2024. However, these numbers don’t consider the several unincorporated communities that are surrounded by or directly adjacent to the incorporated cities that make up the Spokane Municipal Statistical area.

Both areas saw increases in housing stock during this period, with Spokane County’s total housing units increasing by 13.4% to 235,498 units in 2024 compared to just 207,665 units in 2014. Like with the population estimates, this increases to a 16.6% increase from 64,217 units in 2014 to 74,878 units in 2024. Though again, this number doesn’t consider the several unincorporated communities that are surrounded by or directly adjacent to the incorporated cities making up the Spokane Municipal Statistical Area.

Although not a perfect representation, this may indicate a larger trend of people moving closer to cities for their amenities but staying on the outskirts to have more land. This, combined with Spokane County’s double-digit growth rates, could explain why Tekoa’s population growth trends of its similar counterparts in Rural Whitman County.

Table 3.7-3: Spokane County Annual Population and Housing OFM Data (2014-2024)

| Category | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total Pop. | 489,986 | 495,986 | 502,706 | 511,653 | 522,337 | 531,191 | 539,339 | 542,100 | 550,700 | 554,600 | 559,400 |
| House Hold. Pop. | 473,770 | 479,740 | 485,729 | 494,783 | 505,227 | 513,934 | 521,932 | 524,604 | 532,926 | 536,700 | 541,346 |
| Group Quarters Pop. | 16,216 | 16,246 | 16,977 | 16,870 | 17,110 | 17,257 | 17,407 | 17,496 | 17,769 | 17,894 | 18,047 |
| Total Housing Units | 207,665 | 209,684 | 211,809 | 214,847 | 218,387 | 221,382 | 224,019 | 226,818 | 230,091 | 232,843 | 235,498 |
| Occupied Housing Units | 193,690 | 195,978 | 198,254 | 201,834 | 205,981 | 209,376 | 212,470 | 213,558 | 216,946 | 218,482 | 220,373 |
| Ocpcy. Rate (%) | 93.27 | 93.46 | 93.60 | 93.94 | 94.32 | 94.58 | 94.84 | 94.15 | 94.29 | 93.83 | 93.58 |
| Average Pop. Per House | 2.4460 | 2.4479 | 2.4500 | 2.4514 | 2.4528 | 2.4546 | 2.4565 | 2.4565 | 2.4565 | 2.4565 | 2.4565 |

Table 3.7-4: Rural Spokane County Annual Population and Housing OFM Data (2014-2024)

| Category | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Total Pop. | 163,207 | 165,411 | 168,515 | 171,800 | 175,424 | 178,964 | 182,733 | 183,045 | 186,875 | 188,145 | 189,735 |
| House Hold. Pop. | 158,006 | 160,128 | 162,999 | 166,518 | 170,321 | 173,709 | 177,266 | 177,530 | 181,233 | 182,495 | 184,123 |
| Group Quarters Pop. | 5,201 | 5,283 | 5,516 | 5,282 | 5,103 | 5,255 | 5,467 | 5,515 | 5,640 | 5,649 | 5,621 |
| Total Housing Units | 64,217 | 64,922 | 65,932 | 67,166 | 68,512 | 69,707 | 70,967 | 71,898 | 73,189 | 73,676 | 74,878 |
| Occupied Housing Units | 60,146 | 60,901 | 61,933 | 63,242 | 64,658 | 65,897 | 67,198 | 67,295 | 68,765 | 69,245 | 69,905 |
| Ocpcy. Rate (%) | 93.66 | 93.81 | 93.93 | 94.16 | 94.37 | 94.53 | 94.69 | 93.60 | 93.95 | 93.99 | 93.36 |
| Average Pop. Per House | 2.4605 | 2.4665 | 2.4722 | 2.4792 | 2.4860 | 2.4920 | 2.4979 | 2.4692 | 2.4762 | 2.4770 | 2.4590 |

## Population Projection Methodology

To support long-term infrastructure planning, population projections for the City of Tekoa were determined using three different strategies. The first one was developed using historical data from 1990-2024, the second used historical data from 2009-2024, and the third used historical data from 1970-2020. Additionally, WAOFM’s county wide projections were also applied directly to Tekoa’s population. The projections extend over a 5-year period to 2030 and a 20-year period to 2045 to assist in facility capacity planning, particularly for the wastewater treatment infrastructure.

### Data Sources

The first analysis looked at decennial census data from WAOFM from 1990-2024 as 1990 was the low point in Tekoa’s population after its Peak in 1910. The second analysis looked at WAOFM’s intercensal data set from 2009 to 2024, as Tekoa saw a population decline in the late 2000’s that bottomed out the following year in 2010.  A third analysis used data from 1970 to 2024 as that was the data range available through the National Historic Geographic Information Service for the Census Tracts within Spokane County. These three data sources were used in addition to WAOFM’s Medium population forecast as its 2025 forecasted number, since it most closely matched their 2020 postcensal data and estimated population for 2024.  The projections resulting from each method were then compared to an extended linear trendline of Tekoa’s population trendline.

### Method 1: WAOFM’s growth projection

To project future population trends, projections from WAOFM were used. This state agency produces three growth forecasts at the individual county level. The medium growth forecast was chosen as its estimate of 2025 population most closely matched the 2024 postcensal population estimate for Whitman County. These growth rates were then applied to Tekoa’s population using the equation Population = Prev. Pop. * (1+growth rate)YRS.

### Method 2: Decennial Census Data

To project future population trends, historical population for Tekoa was analyzed using Microsoft Excel. A scatter plot and linear trendline were created to capture Tekoa’s relatively steady increase in population since 1990. The best-fit trendline was then used to forecast future population values. By substituting the target years (e.g. 2030 and 2045) into the equation, population projections were generated. This method offers a data-driven approach to long-term planning, ensuring that future trends are estimated based on observed historical patterns, rather than assuming a growth rate. This gave an equation of Population = 1.4949(year)-2204.8 with a statistical correlation value (R2) value of 0.4069. Despite this weak linear correlation, it still tracked well with WAOFM’s medium growth forecast percentages for Whitman County.

Figure 3.8-1: Population Trend Since 1990 Using Decennial Census Data and Whitman County's Projected Growth

### Method : Intercensal Data

To project future population trends, historical population data for Tekoa was analyzed using Microsoft Excel. A Scatter plot and linear trendline were created to capture Tekoa’s relatively steady increase in population since 2009. The best-fit trendline was then used to forecast future population values. By substituting the target years (e.g 2030 and 2045) into the equation, population projections were generated. This method offers a data driven approach to long-term planning, ensuring that future trends are estimated based on historical patterns, rather than assuming a growth rate. This analysis yielded an equation of Population = 2.2603(year)-3756.8 with a statistical correlation value (R2) value of 0.6391 indicating a moderate level of linear correlation over this time frame. The projected population for Tekoa also tracked well with WAOFM’s medium growth forecast percentages for Whitman County.

Figure 3.8-2: Population Trend Since 2009 Using Intercensal Census Data and Whitman County Projected Growth

### Method : Spokane County Population Trends

Due to Tekoa’s proximity to Spokane County, Microsoft Excel was used to organize the total Censual population by census tract from 1970-2020 to determine the censual population or Spokane County outside of the Spokane Metropolitan Statistical Area. This, along with Tekoa’s historical population was then analyzed using Microsoft Excel. A scatter plot and quadratic trendline were created to capture Tekoa’s relatively stagnant population from 1970-2020.  By substituting the target years (e.g 2030 and 2045) into the equation, population projections were generated. This method offers a data driven approach to long-term planning, ensuring that future trends are estimated based on historical patterns, rather than assuming a constant rate of growth. This analysis yielded an equation of Population = 0.03664(year)2 – 146.47353(year) + 147174.95278 with a statistical correlation value (R2) value of 0.1096 indicating a little correlation in Tekoa’s population since 1970. Additionally, this quadratic trendline does not track WAOFM’s medium growth forecast percentages for Spokane County. Additionally, this trendline overestimates Tekoa’s population compared to what WAOFM’s medium growth forecast percentages for Whitman County generate.

Figure 1: Population Trend Since 1970 Using Decennial Census Data and Spokane County's Projected Growth

### Methods 5 & 6: Housing Unit – Based Projection

The fifth method estimates future population based on housing data. It considers the number of total housing units, occupancy rates, and average household size to determine population projections. The formula used is

Population = (Total Housing Units) x (Occupancy) Rate x (Average Household Size)

To estimate the number of future housing units, historical data from WAOFM covering the period from 1990 to 2024 was used, as well as the maximum number of potential new units possible based on the amount of vacant land and its current zoning requirements.

The City of Tekoa currently has 260.5 acres of vacant parcels zones as Rural Residential, and 28.25 acres of vacant parcels zoned as Urban Residential. Per the city zoning code, Rural residential zoning can have up to 2.5 housing units/acre and Urban residential zoning can have up to 5 units per acre. Based on this density, and assuming it does not change over the planning period, the city has zoned land for 651 new rural residential units and 141 new urban residential units. This estimated vacant land does assume that some larger lots with vacant land on them end up subdivided to support the maximum density allowed by their zoning category. It should also be noted that the city does allow residential use of commercially zoned parcels and that this was not considered in this analysis.

Table 3-3: Residential Zoning Summary

Method 5 assumes organic growth throughout the planning period and method 6 assumes that the city will max out its potential for new housing units during the planning period taking place in three 6-year cycles starting in 2027. Forecasting the number of housing units was done using the medium growth forecast from WAOFM. The average occupancy rate and household size over the last 10 years will be assumed as the occupancy rate and vacancy rate throughout the planning period. These values are 87.42% and 2.38 people per household as illustrated in the figure below.

Figure 2: Occupancy Rate and Average Household Size Trend

#### Method 5A, Organic Growth of Housing units

This method assumes that housing units will increase organically as Tekoa continues to grow according to its natural, socio-economic development trends. In this case, the projected population growth is based purely on historical housing data, occupancy rates, and average household sizes. For 2030 the forecasted population is approximately ### people, and by 2045, it is projected to be around ### people

#### Method 5B, Max Buildout of Housing units

This method assumes that the City of Tekoa will be at maximum buildout at the end of the planning period, significantly increasing the number of housing units in Tekoa, starting in 2027 and occurring in 3, 6-year cycles. The following table and figure summarize the projected populations based on an organic growth scenario and a max buildout scenario.

Table 3-4 Tekoa Housing Growth Forecasts

| Year | Method 5: Housing Units (Organic Growth) | Method 6: Housing Units (Max Build Out) | Method 5: Projected Population (Organic Growth) | Method 6: Projected Population (Max Build Out) |
| --- | --- | --- | --- | --- |
| 2030 | 375 | 498 | 833 | 1089 |
| 2035 | 380 | 713 | 844 | 1537 |
| 2040 | 384 | 928 | 853 | 1986 |
| 2045 | 387 | 1143 | 860 | 2433 |

Figure 3: Tekoa Historic Housing Trends and Forecast Housing Units

## Summary

The population projection study for the City of Tekoa utilized six different models based on historical population trends to support long term infrastructure planning. The first method strictly looked at WAOFM’s growth projection for Whitman county, the second used strictly decennial census data from WAOFM from 1990 to present, the third method included intercensal data from WAOFM from 2009 to present, the fourth method used censual data from 1970-present, and the fifth method looked at the available zoned land and how many new housing units could be built under the current zoning. The second two methods compare how the population trended in comparison to Whitman County’s projected growth percentages and the fourth compared it to Spokane County’s projected growth percentages due to its proximity to the Spokane/Whitman County Line. The fifth method looked at historical housing data with organic growth and the sixth method looked at historical housing data with a full buildout of the city. All six approaches provide a data-driven estimate of future population based on observed demographic shifts over time.

| Method | 2030 | 2045 | Use in Design? | Rationale |
| --- | --- | --- | --- | --- |
| M1—OFM County Medium | 832 | 860 | ✓ | State-anchored, conservative |
| M2—Decennial (1990–2024) | 830 | 852 | ✓ | Long-term continuity; aligns with M1 |
| M3—Intercensal (2009–2024) | 832 | 866 | ✓ | Most recent; best fit among Tekoa-only |
| M4—Spokane non-MSA (quad) | 823 | 866 | ✗ | Weak fit; regional proxy only |
| M5A—Housing (Organic) | 833 | 860 | ✓ | Matches M1/M3 via housing lens |
| M5B—Housing (Max Buildout) | 1,089 | 2,433 | Sensitivity only | Upper-bound if large developments occur |

Ta: Summary of Projected Population by Method

| Tekoa Population in Year | WAOFM Medium Forecast Percent Growth for Whitman County | Method |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Method 1 Based on Whitman County’s Growth Forecast | Method 2 Censual Trend 1990-2024 (R2 = 0.4069) | Method 3 Intercensal Trend 2009-2024 (R2 = 0.6361) | Method 4 Censual Trend 1970-2024 (R2 = 0.1061) | Method 5 Housing Based Forecasting (Organic Growth) | Method 6 Housing Based Forecasting (Max Buildout) |
| Equation | N/A | Pop = Prevpop*(1+%Δ) | Pop = 1.4949(year)-2204.8 | Pop = 2.2603(year)-3756.8 | Pop = 0.03664(year)2-146.47353+147174.95278 | Pop = Housing Units * Occ. Rate *Avg. Pop/home | Pop = Housing Units * Occ. Rate *Avg. Pop/home |
| 2030 | 1.52% | 832 | 830 | 832 | 823 | 833 | 1089 |
| 2035 | 1.36% | 844 | 837 | 843 | 836 | 844 | 1537 |
| 2040 | 1.07% | 853 | 845 | 854 | 850 | 853 | 1986 |
| 2045 | 0.83% | 860 | 852 | 866 | 866 | 860 | 2433 |

# PRESENT WASTEWATER CONDITIONS

This section details the current wastewater flows, characteristics, sources, and variations within the Tekoa system.

4.1 Waste Loading

| Parameter | 2022 | 2023 | 2024 | Average (2022-2024) |
| --- | --- | --- | --- | --- |
| Average Annual Daily Flow (AADF) (MGD) | 0.134 | 0.108 | 0.103 | 0.115 |
| Max Month Avg Daily Flow (MMADF) - Dry Season (MGD) | 0.249 | 0.109 | 0.085 |  |
| Max Month Avg Daily Flow (MMADF) - Wet Season (MGD) | 0.179 | 0.196 | 0.188 |  |
| Highest MMADF (Overall) (MGD) | 0.249 | 0.196 | 0.188 |  |
| Peak Day Flow (PDF) (MGD) | 1.18 | 0.99 | 0.3 |  |
| Peak Hourly Flow (PHF) (MGD or GPM) |  |  |  |  |
| Average Influent BOD Loading (lbs/day) | 105.6 | 107.3 | 86.7 | 99.9 |
| Average Influent TSS Loading (lbs/day) | 110.4 | 109.4 | 82.1 | 100.6 |
| Average Influent BOD Concentration (mg/L) | 88.1 | 110.7 | 99.7 | 104.2 |
| Average Influent TSS Concentration (mg/L) | 92.2 | 112.9 | 94.4 | 104.9 |
| Average Influent TKN/Ammonia Concentration (mg/L) |  |  |  |  |
| Average Influent Total Phosphorus Concentration (mg/L) |  |  |  |  |

4.2  Wastewater Sources
The wastewater collected and treated by the Tekoa WWTP is primarily domestic sewage originating from residential customers. Based on available information, there are no significant industrial wastewater contributors to the system.

4.3 Infiltration and Inflow Assessment
Infiltration (groundwater entering leaky pipes/manholes) and Inflow (stormwater entering through direct connections like roof drains or catch basins) add extraneous flows to the sanitary sewer system, particularly during wet weather or high groundwater conditions. High I&I reduces treatment capacity, increases pumping costs, and can contribute to hydraulic overloading.

- Describe I&I study and analysis been conducted recently (for instance,  flow monitoring, smoke testing, manhole inspections)

- Summarize the findings, including estimated I&I rates (for instance,  gallons per acre per day, gallons per capita per day, or percentage of peak flow).

- Describe the general age and condition of the collection system (pipe materials, known problem areas) based on City knowledge or record and summarize the impacts of the recent I
&I study.

## Load and Flow Variations

### Seasonal

Wastewater flows and characteristics in Tekoa exhibit seasonal variations typical of Eastern Washington communities with lagoon systems. Flows are generally higher during the late fall, winter, and spring months due to increased precipitation, snowmelt, and higher groundwater levels contributing to I&I. Conversely, flows are typically lower during the drier summer months. Influent wastewater temperatures are lower in winter, which can reduce the biological treatment efficiency of the lagoon system, potentially impacting BOD and ammonia removal.

### Diurnal

Daily flow patterns (diurnal variations) are typical of predominantly residential communities of the type served by the Tekoa Wastewater Treatment Plant. Flows are lowest during the early morning hours (approx. 1 AM - 5 AM) and typically peak twice: a morning peak between 7 AM - 10 AM and an evening peak between 6 PM - 9 PM, corresponding to periods of highest water use in homes.

# Existing and Projected Wastewater Characteristics

(WAC 173-240-050(3)(h)(i))

## Introduction

The wastewater generated within Tekoa primarily originates from domestic sources, composed primarily of single-family homes.  Additional contributions come from a mix of commercial and institutional sources: local businesses, schools, and public facilities. See Chapter 3 for a summary of the wastewater sources based on DMR data for the years 2022 through Spring 2025. There are no significant industrial discharges to the system nor are any planned at present.

Wastewater treatment is a critical public health and environmental protection service, ensuring that effluent discharged to Hangman Creek meets stringent regulatory standards and minimizes impact on the aquatic environment. This is essential to protect public health, to preserve the ecological balance of receiving waters, and comply with environmental regulations.

This chapter aims to accurately characterize existing wastewater flows and pollutant loads and to project these parameters for the 5 and 20-year planning period to inform this plan’s system evaluation as well as the design of any improvements resulting from the analysis. An accurate understanding of these characteristics is foundational for effective wastewater management.

## Wastewater Flow Characteristic Terms

Understanding various wastewater flow characteristics and pollutant loads is essential for evaluating the performance of the existing system and to design systems that are not only effective under average conditions but can also handle predictable extremes and withstand population or industry growth. Key terms used throughout this plan are defined in Table 5.2-1 below, along with their typical application in wastewater facility planning.

Table 5-1 Wastewater Flow Characterization Definitions

| Parameter | Definition | Source | Formula |
| --- | --- | --- | --- |
| AAF | Average Annual Flow - “The total annual volume divided by 365 days. This value is approximated by the mean of the twelve monthly average flows.” | EPA I&I Guidance. (2014) | Σ Qmonth / 12 |
| ADF | Average Daily Flow - “The average of the daily flow volumes anticipated to occur over a calendar year” | Ecology. (2008). “Orange Book” | Σ Q24h / n |
| AADF | Average Annual Design Flow - “The average of the daily flow volumes anticipated to occur over a calendar year.” | Ecology. (2008). “Orange Book” | Design Planning Value |
| BOD₅ | Five-Day Biochemical Oxygen Demand – “A measure of the amount of oxygen required to stabilize a waste biologically over a 5-d period.” | Metcalf & Eddy/AECOM. (2014) |  |
| TSS | Total Suspended Solids - “Portion of total solids retained on a filter with a specified pore size, measured after being dried at a specified temperature…” | Metcalf & Eddy/AECOM. (2014) |  |
| MWDF | Maximum Week Design Flow - The largest volume of flow anticipated to occur during a continuous 7-day period, expressed as a daily average. | Ecology. (2008). “Orange Book” | Observation |
| MMDF | Maximum Month Design Flow - “The largest volume of flow anticipated to occur during a continuous 30-day period, expressed as a daily average.” | Ecology. (2008). “Orange Book” | Max 30-day rolling window through the design-years |
| MDDF | Maximum Day Design Flow - “The largest volume of flow anticipated to occur during a one-day period, expressed as a daily average.” | Ecology. (2008). “Orange Book” | Observation of measured flows during design years |
| PHDF | Peak Hour Design Flow - “The largest volume of flow anticipated to occur during a one-hour period, expressed as a daily or hourly average.” | Ecology. (2008). “Orange Book” | Measured or PHDF = PFhr × AADF |
| PIDF | Peak Instantaneous Design Flow - “The maximum anticipated instantaneous flow.” | Ecology. (2008). “Orange Book” | Measured or PIDF = PFinst × AADF |
| PF | “Peaking Factor = ratio of peak hourly flow to average daily flow.” | Ecology. (2008). “Orange Book” | PF = QPHF / ADF |
| MWF | “Maximum Week Flow: highest 7-day average flow in one year.” | Tchobanoglous et al. (2003), Table 3-8 | MWF = Σ Q7-d / 7 |
| MMF | “Maximum Month Flow: highest 30-day average flow in one year.” | Tchobanoglous et al. (2003), Table 3-8 | MMF = Σ Q30-d / 30 |

Table 5-2Wastewater I&I Analysis Definitions

| Parameter | Definition | Source | Equation / Derivation |
| --- | --- | --- | --- |
| ADW | Average Dry Weather Flow - “Flow during a period of extended dry weather (7–14 d) and seasonally high groundwater. Flow includes sanitary flow and infiltration, and excludes significant industrial and commercial flows (assumes no inflow during dry weather conditions).” | EPA I/I Guide (2014) | ADW = (Total DWF) / (Dry Period Length) |
| GWI | Groundwater Infiltration (GWI) – “…The average of the low nighttime flows (midnight to 6 am) per day for the same time period, minus significant industrial or commercial nighttime flows.” Because the City doesn’t record hourly flow data, GWI was estimated using the Max Weekly Infiltration (MWI). See below. | EPA I/I Guide (2014) | See MWI |
| BSF | Base Sanitary Flow – “The portion of wastewater which includes domestic, commercial, institutional, and industrial sewage and specifically excludes infiltration and inflow.” | EPA I/I Guide (2014) | BSF = QADWF – QGWI |
| DWF | “All flow in a sewer (includes sanitary flow and infiltration) except that caused directly by rainfall. Measured during a period of extended dry weather (7 to 14 days) and seasonally high groundwater.” | EPA I/I Guide (2014) | QDWF = QS + QGWI |
| Infiltration | Infiltration – “Water other than sanitary wastewater that enters a sewer system from the ground through defective pipes, pipe joints, connections, or manholes. Infiltration does not include inflow.” | EPA I/I Guide (2014) |  |
| Inflow | Inflow - “Water other than sanitary wastewater that enters a sewer system from sources such as roof leaders, cellar/foundation drains, yard drains, area drains, drains from springs and swampy areas, manhole covers, cross connections between storm sewers and sanitary sewers, and catch basins. Inflow does not include infiltration.” | EPA I/I Guide (2014) |  |
| Total I/I | “Infiltration plus inflow - total extraneous wastewater entering the system.” | 40 CFR § 35.2005(b)(20–21) | QI/I = QDWF – BSF |
| Inflow Volume | Inflow Volume - “Total inflow volume for a single event: area between storm hydrograph & dry-weather hydrograph.” | EPA I/I Guide (2014) | ∫(QI/I dt) |
| MWI | Maximum Weekly Infiltration – “The highest daily flow at seasonal high groundwater after a dry period of three days or more minus the base sanitary flow.” | EPA I/I Guide (2014) | Subtract BSF from highest daily flow after a dry period of three days or more during high seasonal groundwater. |
| AWWF | Average Wet-Weather Flow – “ arithmetic mean of daily flows during wet-weather periods.” Wet weather understood to be from November to May for the purposes of this report. | EPA Quick Guide (2014) | QAWWF = Σ Qwet / n |
| PWWF | Peak Wet-Weather Flow – “highest instantaneous flow during a storm (typically 2-hr peak).” | EPA Quick Guide (2014) | — (by observation) |
| RDII | “Rainfall-Induced Infiltration: short-term increase in infiltration as a result of rain.” | Tchobanoglous et al. (2003), Table 3-8 | — |
| WWF | “Highest daily flow during & immediately after a significant storm event.” | Tchobanoglous et al. (2003), Table 3-8 | — (by observation) |

## Wastewater Flow Summary

WAC 173-240-050(3)(g))

Discharge Monitoring Reports (DMRs) from 2022 through 2024 were analyzed to determine historical influent flows to WWTP for the design period. This data, which represents actual measured flows to and from the facility (taken daily), provides the basis for characterizing system hydraulics in this report. The flow data along with OFM population data, was used to generate Table 5.3-1, which summarizes total system flows, average daily flows, estimated total Equivalent Residential Units (ERUs), and the average daily flow per ERU. The table is followed by a

Table 5-3 Summary of Annual Wastewater Flow and ERUs 2022 to 2024

| Year | Total Flow Entire System (MG/Year) | Average Daily Flow (ADF) (gpd) | Total Equivalent Residential Units (ERU) | Average Daily Flow Per ERU (gpd/ERU) |
| --- | --- | --- | --- | --- |
| 2022 | 49.1 | 134,520 | 460 | 292 |
| 2023 | 42.87 | 117,452 | 460 | 255 |
| 2024 | 36.8 | 100,486 | 461 | 218 |

Guidance for ERU estimation and flow analysis was taken from {{ Cite_Guidance_Document, for instance,  Washington State Department of Ecology's "Criteria for Sewage Works Design" (Orange Book) }}. The Orange Book provides standardized methodologies and typical values used in Washington State, ensuring consistency in engineering assessments. <<check>>

The average annual flow to the WWTP over this period was calculated to be {{ Calculated_Average_Annual_Flow }} gpd. This value is utilized for long-term operational planning, estimating annual O&M costs, and as a fundamental baseline for developing flow projections and assessing overall plant loading against its design capacity.

### ERU Calculations

The amount of wastewater generated by a typical single-family home, the Equivalent Residential Unit (ERU) is a fundamental parameter in wastewater planning, representing the daily hydraulic contribution generated by a single home or dwelling.  The ERU flow was estimated in multiple ways to as a check against error and to account for the strengths and weaknesses of each method.  In facility plans, the ERU concept is used to normalize contributions from various types of connections (residential, commercial, institutional) to a common unit, which simplifies the process of projecting future wastewater flows based on anticipated growth in housing and commercial development. Because of the contribution from I&I and other factors such as the larger variety of uses which make up the commercial and industrial units, residential units are the simplest basis to use as a common basis.

### Wastewater ERU

The rationale behind using winter water consumption data for estimating BSF is that outdoor water use, such as landscape irrigation, is minimal or nonexistent during these colder months. Additionally, while groundwater levels might be seasonally high (potentially increasing infiltration), the direct impact of rainfall-induced inflow is generally less compared to wetter storm seasons like spring, making winter flows more representative of sanitary contributions plus persistent infiltration. To account for the normal portion of metered winter water use which typically doesn’t end up in the wastewater system, a factor of .9 was applied to the BSF.

## Inflow and Infiltration Analysis

### Estimating Average Base Sanitary Flow (BSF)

According to Washington State OFM (WAOFM), a typical single-family home in Tekoa is estimated to have an average of 2.22 residents in 2024. Since the City doesn’t collect water meter readings in the winter due to snow and freezing, source (well) data was used to calculate a per unit average.  Although cleanly delineated year-round meter data would be preferable to winter consumption data alone, winter consumption data is preferable to summer data as a basis for ERU calculations since fewer residents are using domestic water for recreation or irrigation.  To adjust for the fact that not all of the water purchased during any season will make it to the drain, a factor of .95 was applied to the resulting figures, which are summarized in Table 5-4 below.

To estimate the Average Base Sanitary Flow (BSF) per ERU, which represents the wastewater flow originating purely from sanitary sources (excluding significant I&I contributions), the previously derived ERU value by the total number of ERU for the year 2024 (461) to arrive at a figure of 87,776 gpd.  See Table 5-4 below.

Table 5-4 BSF Calculation Summary (Method 1)

| Parameter | Notes | Figures |
| --- | --- | --- |
| Total Nov. - Apr. Consumption | From source consumption data | 15,302,000 |
| Residential Consumption Volume (Gal) | Accounts for DSL and removes commercial flow | 12,394,620 |
| Winter Residential Flow (gpd) | Residential consumption divided by 181 days (Nov. through Apr.) | 68,479 |
| Per Capita Winter Residential Flow (gpd) | Assumed 820 population and factored by .95 | 79 |
| Residential ERU (gpd) | Assumes 2.22 persons per household from OFM | 190 |
| Base Sanitary Flow (gpd) | Residential ERU applied to total ERUs (461) | 87,776 |

Table 5-5 I&I Segregation (GWI and RDII)

| Parameter | Formula | Value (MGD) |
| --- | --- | --- |
| Groundwater Infiltration (GWI) | ADWPeak – BSF = GWI | 0.071 |
| Rainfall-Derived Infiltration & Inflow (RDII) | RDII = AWWF - ADWF | 57 |

### Peak Hour Flow

Peak Hour Flow (PHF), also referred to as Peak Hourly Design Flow (PHDF), represents the maximum rate of wastewater flow expected to reach the WWTP or pass through any component of the collection system within a single hour (or sometimes a shorter, more instantaneous peak). This value is critical for the hydraulic design of many components of the sewer system, including pipe diameters, pump capacities, lift station wet well sizing, and the hydraulic capacity of various treatment plant units (for instance,  screens, grit chambers, primary clarifiers), to ensure they can handle these peak loads without overflowing, surcharging, or experiencing operational issues such as reduced treatment efficiency.

Based on an inspection of flow data from 2022 to 2024, the highest peak flows for Tekoa’s system on the dates listed in Table 5.3-3 below. These events occurred during, or shortly after, significant rainfall events, indicating a strong RDII component contributing to the peaks.

Table 5.3-3: Summary of Rainfall Data for Peak Flow Events

| Date | Rainfall Depth (inches) | Notes |
| --- | --- | --- |
| June 13, 2022 | 0.66 | Occurred during a rainfall event from 6/10 to 6/14, two days after a 1.06 inch precipitation event on 6/7 |
| December 2, 2023 | 0.54 | Occurred during a rainfall event from 12/1 to 12/12 |
| January 2, 2024 | 0.05 | Occurred after a 0.5 in rainfall event on 12/31/23 |

5.3.3(a) Peak Hour Flow Calculation

The peak hour flow was calculated by first identifying the highest recorded daily wastewater volume from the 2022 to 2024 sample period. The highest daily volume observed was 1.18 MG on June 13th, 2022. When attributed to the number of active ERUs in 2022, it translates 25,650 gpd/ERU. This daily volume per ERU is then converted to an average daily flow rate in gallons per minute (GPM) for a flow rate of .

To estimate the peak hour flow from this highest average daily flow rate, a diurnal peaking factor is applied. This factor accounts for the typical variations in water use -----------------------0s }}, a peaking factor of {{ Peaking_Factor_Value, for instance,  using the Harmon formula, Babbitt formula, or a typical range like 2.5 to 4.0 for smaller systems }} was used.
Therefore, Peak Hour Flow (GPM) = (Highest Daily Flow Rate in GPM) ×[;

‘me_of_Town/Utility }}, this results in a calculated Peak Hour Flow of {{ ‘/8 }} GPM.

5.3.3(b) Assumptions and Simplifications

The following assumptions were made in the derivation of the peak hour flow calculations:

- It was assumed that contributions from {{ Commercial_Institutional_Sources_Assumption, for instance,  commercial and institutional sources within the service area exhibit similar diurnal peaking patterns to residential flows, or their contribution to the overall peak flow is relatively small and thus adequately accounted for within the selected overall peaking factor }}. This is because {{ Rationale_Commercial, for instance,  the service area is predominantly residential with limited large commercial/institutional users that would have significantly different peak discharge times }}. <<check>>

- It was assumed that there are {{ No/Minimal }} significant industrial dischargers whose batch discharges or unique operational schedules could disproportionately affect or create atypical peak flows outside the normal diurnal pattern. This is based on {{ Rationale_Industrial, for instance,  a review of connected users and discharge permits }}. <<check>>

- The applied peaking factor is representative of the combined diurnal wastewater generation patterns for the mix of users in {{ Name_of_Town/Utility }}. <<check>>

### Minimum Flow

Calculating daily minimum flows is necessary to ensure that self-cleansing velocities are maintained within the gravity portions of the sewer collection system, preventing the deposition of solids and subsequent blockages, odor issues, and corrosion. It is also important for the proper operation of pumps (to avoid excessive short-cycling which can damage equipment) and some treatment processes that may be sensitive to very low flow conditions or require a minimum hydraulic throughput.

Based on the inspection of flow data from 2022 to 2024, the minimum daily influent volume for the period under consideration was on August 23rd, 2024.  This value was divided by the 2024 ERUs to produce a minimum daily flow per ERU to arrive at a value of {{ Minimum_Daily_Flow_per_ERU }} gpd/ERU, or approximately 24.2 gpm per capita (assuming {{ Avg_Persons_per_ERU }} persons/ERU).

To estimate a "peak hour minimum flow," or more accurately, the lowest instantaneous flow expected during the diurnal cycle on a minimum flow day, the minimum average daily flow rate is considered. Even during the day with the lowest total flow, there will still be diurnal variations with very low flows typically occurring in the late-night/early-morning hours. <<check>> This can be estimated using a minimum diurnal factor (for instance,  {{ Minimum_Diurnal_Factor_Value, for instance,  0.25 to 0.5 }} times the average flow on that minimum day). This minimum instantaneous flow is the critical condition for assessing if velocities in sewers are sufficient to prevent solids deposition, especially in flatter gradient pipes.

Ensuring adequate cleansing velocity (typically around 2 feet per second when flowing at least half full for sanitary sewers) at minimum flow conditions is important because it helps maintain the operational efficiency and longevity of the collection system. It prevents the buildup of solids, which can lead to reduced pipe capacity, accelerated corrosion from septic conditions, nuisance odor generation, and an increased need for costly and disruptive sewer cleaning operations.

### Dry Weather Flow

Average Dry Weather Flow (ADWF) is defined as the total wastewater flow entering the treatment facility during an extended dry period, typically lasting 7 to 14 consecutive days, when direct rainfall-induced inflow is negligible. This flow consists of the true sanitary flow (Qs) generated by residential, commercial, and institutional users, combined with groundwater infiltration (QGWI) that may seep into the collection system through pipe defects, joints, or manholes, especially when groundwater levels are seasonally high. It explicitly excludes significant, direct commercial or industrial process discharges that are not part of the baseline sanitary load, if any.

The assumption of "no additional inflow" during dry weather conditions is critical for isolating the sanitary and groundwater infiltration components. Inflow is primarily associated with direct stormwater entry into the sanitary sewer system, commonly from sources such as improperly connected sump pumps, roof leaders, foundation drains, or cross-connections with storm drains, all of which are activated by precipitation events. By analyzing flow during periods without rainfall, these direct inflow contributions are minimized or eliminated, allowing for a more accurate assessment of the baseline wastewater generation and persistent infiltration. <<check>>

Quantitatively, ADWF can be represented as:
ADWF = Qs + QGWI
Where:

- ADWF = Average Dry Weather Flow (gpd)

- Qs = Base Sanitary Flow from domestic, commercial, and institutional sources (gpd)

- QGWI = Groundwater Infiltration (gpd)

The process of deriving ADWF for {{ Name_of_Town/Utility }} involved a review of historical Discharge Monitoring Reports (DMRs) for the period {{ Start_Year_DMR_Analysis_ADWF }} to {{ End_Year_DMR_Analysis_ADWF }}, in conjunction with daily precipitation data from the {{ NOAA_Station_Name_ADWF }} weather station for the same period. A continuous dry period, defined as at least {{ Min_Dry_Days_for_ADWF, for instance,  7 to 14 }} days with no measurable precipitation (or precipitation below a minimal threshold of {{ Max_Precip_Threshold_for_Dry_Day, for instance,  0.01 inches }}), was identified. The average daily influent flow recorded at the WWTP during this identified period was then calculated to determine the ADWF. This methodical selection ensures the data represents true dry weather conditions. <<check>>

Table {{ Table_Number_ADWF_Data }}: Total Dry Weather Flow Data for Selected Period

| Date | Day of Week | ADWF (gpd) |
| --- | --- | --- |
| {{ ADWF_Date_1 }} | {{ ADWF_Day_1 }} | {{ ADWF_Flow_1 }} |
| {{ ADWF_Date_2 }} | {{ ADWF_Day_2 }} | {{ ADWF_Flow_2 }} |
| {{ ADWF_Date_3 }} | {{ ADWF_Day_3 }} | {{ ADWF_Flow_3 }} |
| ... | ... | ... |
| {{ ADWF_Date_N }} | {{ ADWF_Day_N }} | {{ ADWF_Flow_N }} |
| Average ADWF |  | {{ Calculated_ADWF_Value }} |

The period from {{ ADWF_Period_Start_Date }} to {{ ADWF_Period_End_Date }} (summarized in Table {{ Table_Number_ADWF_Data }}) was chosen for ADWF calculation as it represented {{ Number_of_Dry_Days_in_Period }} consecutive days without significant precipitation and the recorded flows during this time did not exhibit anomalous spikes or drops that might indicate unusual operational conditions or unrecorded minor precipitation events. Such consistency is key to obtaining a representative ADWF value. <<check>>

The calculated ADWF for {{ Name_of_Town/Utility }} is {{ Calculated_ADWF_Value }} gpd. Based on the estimated population of {{ Population_at_Time_of_ADWF_Period }} during this period, the ADWF per capita is approximately {{ ADWF_per_Capita_Value }} gallons per capita per day (gpcd). This figure gives an indication of the average daily water use per person that enters the sewer system from sanitary sources, combined with any groundwater infiltration occurring during these dry conditions. It is a baseline measure of system loading absent storm impacts. <<check>> The U.S. Environmental Protection Agency (EPA) often uses a benchmark of 120 gpcd for evaluating infiltration and inflow (I/I), as outlined in documents like the "Handbook for Sewer System Infrastructure Analysis and Rehabilitation" (EPA/625/6-91/030) or similar I/I analysis guidance. <<check>> This 120 gpcd value typically includes a component for reasonable base sanitary flow (for instance,  an average of 70-80 gpcd nationwide, though this can vary regionally) and an allowance for non-excessive groundwater infiltration (for instance,  around 40-50 gpcd, or a common design allowance like 500-1500 gallons per day per inch-mile of sewer). <<check>> Comparing the calculated {{ ADWF_per_Capita_Value }} gpcd to this EPA guideline suggests that {{ Interpretation_of_Comparison_to_120_gpcd, for instance,  "groundwater infiltration may be a manageable component of the dry weather flow," or "groundwater infiltration appears to be a significant contributor, warranting further investigation," or "the per capita flow is well below the guideline, indicating a relatively tight system during dry weather which is positive but should be verified against expected sanitary flows." }} <<check>> Further investigation into I/I sources is detailed in Chapter {{ Chapter_Number_for_I_I_Analysis }}.

An ADWF significantly below expected sanitary flow could indicate issues such as exfiltration in parts of the system or unusually low per capita water use, while an ADWF significantly above expected sanitary flow points towards higher levels of groundwater infiltration. <<check>>
<<INSERT DISCUSSION ABOUT LEAKY MANHOLES HERE: Manholes, especially older brick or precast concrete structures, can be major sources of groundwater infiltration even during dry weather if the surrounding water table is above the manhole invert or defects in the structure. Common defects include cracked barrels, deteriorated mortar in brick manholes, leaking pipe-to-manhole seals (often called "boots" or gaskets), and compromised frame-to-cone seals. During seasonally high groundwater, water can seep continuously through these defects. If the ADWF is considerably higher than the estimated Base Sanitary Flow (BSF), it strongly suggests that such persistent infiltration from sources like leaky manholes and pipe joints is a significant contributor to the total flow. Findings from any closed-circuit television (CCTV) inspections or smoke/dye testing that identified active infiltration at manholes would be referenced here to support this. For example, "CCTV inspections conducted in {{Year}} identified {{Number}} manholes in the {{Area_Name}} basin exhibiting signs of active infiltration under dry weather conditions." This sets the stage for targeted manhole rehabilitation as an I/I reduction strategy.>> <<check>>

### Wet Weather Flow

Rainfall-Derived Infiltration and Inflow (RDII) is the extraneous surface and groundwater that enters the sanitary sewer system exclusively as a direct consequence of precipitation events. It is composed of two primary components:

- Inflow: Stormwater that enters the sewer system rapidly and directly. Common sources include direct connections like roof leaders, yard drains, catch basins connected to the sanitary sewer, sump pumps improperly discharged to the sanitary sewer, holes in manhole covers, or structurally failed pipes that allow surface water to pour in.

- Infiltration: Groundwater that enters the system more slowly through defects below the ground surface, such as cracks in pipes, deteriorated pipe joints, faulty service connections, and leaky manholes. The rate of this infiltration is often exacerbated by a rise in the groundwater table due to prolonged or intense rainfall saturating the surrounding soil.

RDII is a major concern in wastewater management as it can consume valuable hydraulic capacity in both the collection system pipes and the WWTP. Excessive RDII can lead to sanitary sewer overflows, cause basement backups, reduce treatment efficiency at the WWTP due to dilution and hydraulic overloading, and significantly increase pumping and treatment operational costs.

Mathematically, the total Wet Weather Flow (WWF) during a storm event can be expressed by considering RDII along with the base flow components:
WWF = Qs + QGWI + QRDII
Where:

- WWF = Total Wet Weather Flow (for instance,  in gpd) during the event.

- Qs (gpd) = Base Sanitary Flow (gpd) – the component from user discharges.

- QGWI (gpd) = Groundwater Infiltration (gpd). QGWI is the persistent infiltration component typically present even in dry weather, though it may increase during wet weather due to higher groundwater tables.

- QRDII (gpd) = Rainfall-Derived Infiltration and Inflow is the additional flow directly attributable to the rainfall event.

To perform the wet weather flow analysis for Tekoa’s collection system, daily precipitation data from the Rosalia NOAA weather station (Station ID: {{ NOAA_Station_ID_Rosalia }}) for the period 2022 to 2024 was correlated with influent flow data recorded at the Tekoa’s WWTP as reported in DMRs. The Rosalia station is considered representative for regional precipitation patterns affecting the service area.

Wet Weather Flow (WWF) is qualitatively defined as the significantly increased and often rapidly fluctuating flow observed at the WWTP during and immediately following a rainfall event. This flow includes the normal ADWF components (sanitary flow and baseline groundwater infiltration) plus the additional, often substantial, volume contributed by RDII. The magnitude, timing (how quickly the flow responds to rain), and duration of the WWF response depend on numerous factors. These include rainfall intensity, total rainfall volume, and duration; antecedent moisture conditions (how saturated the ground was before the storm); the physical condition and age of the sewer system (more defects lead to more I&I); soil types and geology; groundwater levels; the topography of the service area; and the extent of directly connected impervious surfaces.

The analysis of WWF for {{ Name_of_Town/Utility }} involved identifying peak flow events from the DMR data that corresponded with significant rainfall events recorded at the Rosalia station. For example, during the storm event of {{ Date_of_Peak_WWF_Storm }}, which recorded {{ Rainfall_Amount_Peak_WWF_Storm }} inches of rain, the peak WWF per capita was calculated to be {{ Peak_WWF_per_Capita_Value }} gpcd. The EPA guidance (for instance,  from I/I analysis handbooks) often suggests that peak wet weather flows exceeding approximately 275 gpcd may be indicative of excessive I/I within a system. <<check>> This 275 gpcd is a general guideline and local conditions or specific permit requirements might dictate other thresholds for "excessive." <<check>> The calculated peak WWF of {{ Peak_WWF_per_Capita_Value }} gpcd for {{ Name_of_Town/Utility }} {{ Comparison_to_EPA_275_gpcd, for instance,  "is below this EPA guideline, suggesting that while RDII is clearly present and contributes to peak flows, it might not be categorized as 'excessive' by this particular metric alone. However, any amount of RDII consumes capacity and should be managed," or "approaches this EPA guideline, indicating that RDII is a significant concern and likely warrants focused mitigation efforts to prevent future capacity issues or SSOs," or "exceeds this EPA guideline, strongly indicating that the system experiences excessive I/I during significant storm events, which necessitates comprehensive investigation and rehabilitation." }} <<check>> Compared to previous I/I studies or facility plans conducted for {{ Name_of_Town/Utility }} in {{ Year_of_Previous_Study, if any }}, the current RDII response {{ Improvement_Status_Compared_to_Previous_Studies, for instance,  "appears to have remained relatively consistent with historical findings, suggesting that past rehabilitation efforts have maintained but not significantly reduced overall RDII," or "shows some improvement in peak flow reduction, potentially due to targeted rehabilitation efforts in Basin X following the {{Year_of_Previous_Study}} study," or "indicates a potential worsening trend in overall RDII response, possibly due to aging infrastructure or new problematic connections." }} <<check>> A detailed I/I analysis, including hydrograph separation to quantify RDII volumes and identification of priority areas for investigation and rehabilitation, is presented in Chapter {{ Chapter_Number_for_I_I_Analysis }}.

| Flow Parameter | 2025 Unit Flow gal/ERU | 2025 | 2031 | 2039 | 2045 |
| --- | --- | --- | --- | --- | --- |
|  |  | Daily Average (gal/day) |  |  |  |
| Average Daily Flow (AADF) |  |  |  |  |  |
| Base Sanitary Flow (BSF) |  |  |  |  |  |
| Average Dry Weather Flow (ADWF) |  |  |  |  |  |
| Maximum Dry Weather Flow (MDWF) |  |  |  |  |  |
| Average Wet Weather Flow (AWWF) |  |  |  |  |  |
| Maximum Week Flow |  |  |  |  |  |
| Maximum Month Flow (MMF) |  |  |  |  |  |
| Flow Parameter | 2025 Unit Flow (gpm/ERU) | 2025 | 2031 | 3039 | 2045 |
|  |  | Flow Rate (gpm) |  |  |  |
| Peak Wet Weather Flow (PWWF) |  |  |  |  |  |
| Peak Hour Design Flow (PHDF) |  |  |  |  |  |
| Peak Instantaneous Design Flow (PIDF) |  |  |  |  |  |
| Minimum Flow |  |  |  |  |  |

# Alternatives Analysis

## Land-Based Disposal Methods

### No-Action Alternative

As state previously, Tekoa’s wastewater treatment plant largely operates within the limits of the current NPDES permit, with

In evaluating potential methods for managing treated wastewater effluent from the City of Tekoa facility, the analysis was performed in light of two reports issued by Ecology which are likely to inform the next NPDES permit to be issued on the facility.  During the restricted discharge period (June-October), various land-based application and treatment systems were considered. A preliminary screening was conducted using the USDA Soil Resource Report for the farmland surrounding Tekoa (See Appendix X) to assess fundamental site suitability based on soil types, topography, and other limitations. This analysis compared site characteristics against the general requirements for different land application methods as outlined in the Washington State Department of Orange Book and other recommended guidance documents, including the Design Criteria for Municipal Wastewater Land Treatment Systems for Public Health Protection (DOH, 1994) and principles from the Guidelines for Preparation of Engineering Reports for Industrial Wastewater Land Application Systems (Ecology 93-36).

Based on this screening, Slow Rate Treatment of Wastewater and Disposal of Wastewater by Irrigation was identified as the only potentially viable land-based alternatives warranting further investigation.

Design of land application systems via irrigation requires thorough site soils testing to characterize the site’s feasibility for land application or land treatment.  The following tests should be performed prior to purchase of selection of a site:

- If the site’s design is such that irrigation quantities will be at or below the site’s agronomic rate:

- Hydrogeologic study.  This requirement can be waived if the site’s discharge has a “limited potential to contaminate”.

- Monitoring Plan.

Both methods rely on the soil-plant matrix for nutrient uptake and additional water treatment. The USDA report indicated that Map Unit 64 (Palouse silt loam) was rated "Not limited" for irrigation and only "Somewhat limited" for slow rate treatment, with the limitation being minor slope constraints primarily affecting surface (non-sprinkler) application. This soil type generally possesses moderate permeability and water holding capacity suitable for crop uptake, aligning with characteristics common for sites using slow rate systems. Map Unit 87 (Schumacher silt loam) was also rated "Somewhat limited" for both uses. While Map Unit 87 is potentially usable, noted limitations include moderate depth to bedrock (40-60 inches) and slower water movement. According to the recommended guidance documents, these factors necessitate careful site-specific design, and likely involving implementing lower hydraulic and nutrient loading rates than Unit 64 to prevent breakthrough to groundwater or perched saturation above the bedrock prior to effective treatment. The slopes in Map Unit 87 would also require careful consideration for irrigation design to minimize runoff. While these units (64 and 87) show some potential, the limited available acreage of Unit 64 and the specific limitations of Unit 87 necessitate rigorous field investigation to confirm suitability and determine actual design loading rates. Map Unit 1010 (Caldwell-Thatuna complex), although rated "Somewhat limited", presents significant challenges related to high water tables and flooding risk, making it considerably less desirable and likely requiring extensive, potentially cost-prohibitive controls (such as underdrainage) inconsistent with typical land treatment feasibility for small systems.

Other land application methods were excluded based on incompatibilities between their requirements and the site's prevailing soil and topographic characteristics. Disposal of Wastewater by Rapid Infiltration was deemed unsuitable due to "Very limited" ratings across all map units. Rapid infiltration systems require highly permeable soils, such as sands and gravels, capable of accepting high hydraulic loading rates. The dominant soil types identified in the Tekoa area are characterized by moderate to moderately slow permeability. Applying high volumes of water typical of rapid infiltration to these finer soils would inevitably lead to prolonged surface ponding and runoff.

Overland Flow Treatment was also eliminated during the screening process. This method relies on using slowly permeable soils (typically clays or clay loams) on carefully graded, uniform slopes (generally 2-8%) to allow wastewater to flow in a thin sheet across the vegetated surface, which allows for treatment through biological action and sedimentation before collection as runoff. The Tekoa area soils are predominantly silt loams, lacking the required low permeability for sheet flow generation. Furthermore, the regional topography features many hills and buttes, with variable and often steeper slopes than ideal for controlled overland flow. The combination of unsuitable soil permeability and challenging topography makes overland flow technically infeasible for this location.

Therefore, based on this initial screening assessment integrating USDA soil data with established land application/treatment principles and criteria from Ecology and DOH guidance, only Slow Rate Treatment and Disposal by Irrigation demonstrate sufficient potential compatibility with site conditions to be carried forward for detailed hydrogeologic investigation and comparative analysis within this Facility Plan.

APPENDIX A

VICINITY MAP

APPENDIX B

SITE MAPS

APPENDIX C

APPENDIX D

CALCULATIONS

APPENDIX E

SEPA CHECKLIST

APPENDIX F